## GSP List
GSP | GSP Name | GSP NRN | Primary Nrn | Primary Name | GSP | PI Exp | PI tag1 | PI tag2 | PI tag3 | PI tag4 | PI tag5 | PI tag6 | PI tag7 | PI tag8
ABNE | Abernethy | 241 | 242 | ABERNETHY | FALSE | ('241~T1~AMPS~AI')*1.732*0.011 | PI tag1: 241~T1~AMPS~AI
ABNE | Abernethy | 241 | 241 | ABERNETHY GRID | TRUE | Aberfeldy Primary substation 2018-19 (11KV DG) | Tags | 267~T1~AMPS~AI | 267~T2~AMPS~AI | Settlements Data | 267A~C01~AMPS~AI |  |  |  |  | Abernethy Primary substation 2018-19 | 241~T1~AMPS~AI
ABNE | Abernethy | 241 | 255 | BALBEGGIE | FALSE | ('255~T1~MW~AI') | PI tag1: 255~T1~MW~AI
ABNE | Abernethy | 241 | 284 | BINN HILL LANDFILL | FALSE | ('284~CS1~MW~AI') | PI tag1: 284~CS1~MW~AI
ABNE | Abernethy | 241 | 279 | BRIDGE OF EARN | FALSE | ('279~003~AMPS~AI'+'279~004~AMPS~AI')*1.732*0.011 | PI tag1: 279~003~AMPS~AI; PI tag2: 279~004~AMPS~AI
ABNE | Abernethy | 241 | 254 | ERROL | FALSE | ('254~SUMM~AMPS~AI')*1.732*0.011 | PI tag1: 254~SUMM~AMPS~AI
ABNE | Abernethy | 241 | 273 | GLENDEVON | FALSE | ('273~11KV~AMPS~AI')*1.732*0.011 | PI tag1: 273~11KV~AMPS~AI
ABNE | Abernethy | 241 | 247 | HARBOUR | FALSE | ('247~T1~AMPS~AI')*1.732*0.011 | PI tag1: 247~T1~AMPS~AI
ABNE | Abernethy | 241 | 251 | MILNATHORT | FALSE | ('251~011~AMPS~AI'+'251~4L5~AMPS~AI')*1.732*0.011 | PI tag1: 251~011~AMPS~AI; PI tag2: 251~4L5~AMPS~AI
ABNE | Abernethy | 241 | 252 | RUMBLING BRIDGE | FALSE | this is not a brimary but a junction point
ABNE | Abernethy | 241 | 271 | SCONE | FALSE | ('271~common~AMPS~AI')*1.732*0.011 | PI tag1: 271~common~AMPS~AI
ALNE | Alness | 502 | 552 | BALALDIE | FALSE | ('552~097~AMPS~AI'+'552~098~AMPS~AI'+'552~099~AMPS~AI')*1.732*0.011 | PI tag1: 552~097~AMPS~AI; PI tag2: 552~098~AMPS~AI; PI tag3: 552~099~AMPS~AI
ALNE | Alness | 502 | 502 | ALNESS GRID | TRUE | Doesn’t seem to exist anymore | PI tag1: 502~6L5~MW~AI
ALNE | Alness | 502 | 541 | CONTULLICH | FALSE | no PI tag
ALNE | Alness | 502 | 551 | CROSSHILLS | FALSE | ('551~T1_T2~AMPS~AI')*1.732*0.011 | PI tag1: 551~T1_T2~AMPS~AI
ALNE | Alness | 502 | 522 | GLASTULLICH | FALSE | ('522~11KV~AMPS~AI')*1.732*0.011 | PI tag1: 522~11KV~AMPS~AI
ALNE | Alness | 502 | 559 | INVERGORDON | FALSE | ('559~T1_T2~AMPS~AI')*1.732*0.011 | PI tag1: 559~T1_T2~AMPS~AI; PI tag2: 559A~001~MW~AI; PI tag3: 559A~002~MW~AI
ALNE | Alness | 502 | 576 | LEALTY | FALSE
ALNE | Alness | 502 | 554 | NIGG | FALSE | ('554~TR1~AMPS~AI')*1.732*0.011 | PI tag1: 554~TR1~AMPS~AI
ALNE | Alness | 502 | 553 | PEDDIESTON | FALSE | ('553~T1~AMPS~AI')*1.732*0.011 | PI tag1: 553~T1~AMPS~AI
ALNE | Alness | 502 | 546 | TAIN | FALSE | ('546~T1_T2~AMPS~AI')*1.732*0.011 | PI tag1: 546~T1_T2~AMPS~AI
ARBR | Arbroath | 61 | 64 | CARNOUSTIE | FALSE | ('064~TR1~MW~AI'+'064~TR2~MW~AI') | PI tag1: 064~TR1~MW~AI; PI tag2: 064~TR2~MW~AI
ANSU | AN SUIDHE | 353 | 353 | AN SUIDHE GRID | TRUE | Aultbea substation 2018-19 (MW Tag) | PI tag1: 504~T1~MW~AI
ARBR | Arbroath | 61 | 61 | ARBROATH GRID | TRUE | Aviemore Primary substation 2018-19 (New Tag) | 704~TR1~MW~AI | 704~TR2~MW~AI | 704~013~AMPS~AI | 704~014~AMPS~AI | 704~015~AMPS~AI | 704~016~AMPS~AI | 704~017~AMPS~AI
ARBR | Arbroath | 61 | 62 | CHARLES AVENUE | FALSE | ('062~T1_T2_11~AMPS~AI')*1.732*0.011 | PI tag1: 062~T1_T2_11~AMPS~AI
ARBR | Arbroath | 61 | 68 | ELLIOT DEPOT | FALSE | ('068~T1_11~AMPS~AI')*1.732*0.011 | PI tag1: 068~T1_11~AMPS~AI
ARBR | Arbroath | 61 | 67 | HUME STREET | FALSE | ('067~T1_T2_11~AMPS~AI')*1.732*0.011 | PI tag1: 067~T1_T2_11~AMPS~AI
ARBR | Arbroath | 61 | 66 | REDFORD | FALSE | ('066~T1_11~AMPS~AI')*1.732*0.011 | PI tag1: 066~T1_11~AMPS~AI
ARMO | Ardmore | 622 | 671 | AIRD | FALSE | ('671A~C01~AMPS~AI'+'671A~C01~AMPS~AI')*1.732*0.011 | PI tag1: 671A~C01~AMPS~AI; PI tag2: 671A~C01~AMPS~AI
ARDK | Ardkinglas | 354 | 354 | BUNARKAIG | TRUE
ARMO | Ardmore | 622 | 622 | ARDMORE GRID | TRUE
ARMO | Ardmore | 622 | 669 | ARNISH | FALSE | ('669~TR1~MW~AI') | PI tag1: 669~TR1~MW~AI
ARMO | Ardmore | 622 | 659 | BARRA G S | FALSE | ('659~TOTAL~MW~AI') | PI tag1: 659~TOTAL~MW~AI
ARMO | Ardmore | 622 | 651 | BARVAS | FALSE | ('651~T1_T2~AMPS~AI')*1.732*0.011 | PI tag1: 651~T1_T2~AMPS~AI; PI tag2: 651~T1~AMPS~AI; PI tag3: 651~T2~AMPS~AI
ARMO | Ardmore | 622 | 652 | BATTERY POINT | FALSE | ('652~T1~MW~AI') | PI tag1: 652~T1~MW~AI; PI tag2: 652~T2~MW~AI; PI tag3: 652~T3~MW~AI
ARMO | Ardmore | 622 | 670 | CALLANISH | FALSE | ('670~011~AMPS~AI')*1.732*0.011 | PI tag1: 670~011~AMPS~AI; PI tag2: 670A~C01~AMPS~AI; PI tag3: 670A~C01~MW~AI
ARMO | Ardmore | 622 | 653 | CLACHAN | FALSE | ('653~TR2~AMPS~AI')*1.732*0.011 | PI tag1: 653~TR2~AMPS~AI
ARMO | Ardmore | 622 | 672 | COLL | FALSE | ('672~TR1~AMPS~AI')*1.732*0.011 | 672~TR1~AMPS~AI | 672A~C01~AMPS~AI | 672A~C01~MW~AI | 672~011~AMPS~AI | 672~012~AMPS~AI
ARMO | Ardmore | 622 | 644 | DRIMORE | FALSE | ('644~T1~AMPS~AI')*1.732*0.011 | PI tag1: 644~T1~AMPS~AI
ARMO | Ardmore | 622 | 666 | EOLIGARRY PMR | FALSE
ARMO | Ardmore | 622 | 663 | FROBOST REGULATOR | FALSE
ARMO | Ardmore | 622 | 648 | GISLA | FALSE | ('648~1H0~AMPS~AI')*1.732*0.011 | PI tag1: 648~1H0~AMPS~AI; PI tag2: 648~G1~KW~AI
ARMO | Ardmore | 622 | 647 | HARRIS GRID | FALSE
ARMO | Ardmore | 622 | 657 | LAXAY | FALSE | ('657~T1~AMPS~AI')*1.732*0.011 | PI tag1: 657~T1~AMPS~AI
ARMO | Ardmore | 622 | 665 | LOCH CARNAN | FALSE
ARMO | Ardmore | 622 | 650 | MAARUIG | FALSE
ARMO | Ardmore | 622 | 667 | NORTHBAY PMR | FALSE
ARMO | Ardmore | 622 | 660 | POLLACHAR | FALSE | ('660~TR1~AMPS~AI')*1.732*0.011 | PI tag1: 660~TR1~AMPS~AI
ARMO | Ardmore | 622 | 664 | RODIL PMR | FALSE
ARMO | Ardmore | 622 | 658 | STOCKINISH | FALSE | ('658~MW~MW~AI') | PI tag1: 658~MW~MW~AI
ARMO | Ardmore | 622 | 645 | STORNOWAY GRID | FALSE
ARMO | Ardmore | 622 | 662 | TARBERT | FALSE | ('662~T1_T2~AMPS~AI')*1.732*0.011 | PI tag1: 662~T1_T2~AMPS~AI
BEAU | Beauly | 506 | 501 | AIGAS | FALSE
BEAU | Beauly | 506 | 509 | BLACKSTAND | FALSE | ('509~TR1~AMPS~AI')*1.732*0.011 | PI tag1: 509~TR1~AMPS~AI
BEAU | Beauly | 506 | 506 | BEAULY GRID | TRUE | Blairlinnans Primary substation 2018-19 | PI tag1: 220~011~AMPS~AI; PI tag2: 220~011~AMPS~AI; PI tag3: 220~011~VOLTS~AI |  | Dingwall Primary substation 2018-19 (11kV DG) | Little Wyvis | Falls of Conis
BEAU | Beauly | 506 | 513 | CONON BRIDGE | FALSE | ('513~TR1~MW~AI'+'513~TR2~MW~AI') | PI tag1: 513~TR1~MW~AI; PI tag2: 513~TR2~MW~AI
BEAU | Beauly | 506 | 515 | DINGWALL | FALSE | ('515~T1~AMPS~AI'+'515~T2~AMPS~AI')*1.732*0.011 | PI tag1: 515~T1~AMPS~AI; PI tag2: 515~T2~AMPS~AI
BEAU | Beauly | 506 | 520 | KILTARLITY | FALSE | ('520~001~AMPS~AI'+'520~002~AMPS~AI')*1.732*0.011 | PI tag1: 520~001~AMPS~AI; PI tag2: 520~002~AMPS~AI
BEAU | Beauly | 506 | 538 | MARYBANK | FALSE | ('538~TR1~AMPS~AI')*1.732*0.011 | PI tag1: 538~TR1~AMPS~AI; PI tag2: 538~011~AMPS~AI; PI tag3: 538~012~AMPS~AI; PI tag4: 538~T1~AMPS~AI
BEAU | Beauly | 506 | 547 | MUIR OF ORD | FALSE | ('547~T1_T2~AMPS~AI')*1.732*0.011 | PI tag1: 547~T1_T2~AMPS~AI
BEAU | Beauly | 506 | 542 | MUIREND | FALSE | ('542~TR1~AMPS~AI')*1.732*0.011 | PI tag1: 542~TR1~AMPS~AI
BEAU | Beauly | 506 | 558 | NORTH KESSOCK | FALSE | ('558~TR1~AMPS~AI')*1.732*0.011 | PI tag1: 558~TR1~AMPS~AI
BOAG | Boat of Garten | 707 | 704 | AVIEMORE | FALSE | ('704~TR1~MW~AI'+'704~TR2~MW~AI') | 704~TR1~MW~AI | 704~TR2~MW~AI | 704~013~AMPS~AI | 704~014~AMPS~AI | 704~015~AMPS~AI | 704~016~AMPS~AI | 704~017~AMPS~AI
BERB | Berryburn | 893 | 893 | BERRYBURN GRID | TRUE | Brechin Primary substation 2018-19 | PI tag1: 073~TR1~MW~AI; PI tag2: 073~TR2~MW~AI
BOAG | Boat of Garten | 707 | 706 | BALLINDALLOCH | FALSE | ('706~TR1~MW~AI'+'706~TR2~MW~AI') | PI tag1: 706~TR1~MW~AI; PI tag2: 706~TR2~MW~AI
BOAG | Boat of Garten | 707 | 708 | BOAT OF GARTEN 11 kV | FALSE | ('707~T1~MW~AI'+'707~T2~MW~AI') | PI tag1: 707~T1~MW~AI; PI tag2: 707~T2~MW~AI
BOAG | Boat of Garten | 707 | 707 | BOAT OF GARTEN GRID | TRUE | Bridge of Dun Primary substation 2018-19 | PI tag1: 072~T1_11~AMPS~AI |  | Boat of Garten Primary substation 2018-19 | 707~T1~MW~AI | 707~T2~MW~AI
BOAG | Boat of Garten | 707 | 777 | DALWHINNIE | FALSE | ('777~011~AMPS~AI')*1.732*0.011 | PI tag1: 777~011~AMPS~AI; PI tag2: 777~11KV~CURRENT~AI
BOAG | Boat of Garten | 707 | 722 | GRANTOWN | FALSE | ('722~T1_T2~AMPS~AI')*1.732*0.011 | PI tag1: 722~T1_T2~AMPS~AI
BOAG | Boat of Garten | 707 | 727 | KINGUSSIE | FALSE | ('727~1H0~MW~AI'+'727~2H0~MW~AI') | 727~1H0~MW~AI | 727~2H0~MW~AI | 727~1H0~AMPS~AI |  |  | 727~1H0~MW~AI | 727~2H0~AMPS~AI
BOAG | Boat of Garten | 707 | 738 | TOMATIN | FALSE | ('738~1H0~AMPS~AI')*1.732*0.011 | PI tag1: 738~1H0~AMPS~AI
BRCW2 | Braco West | 201 | 210 | CALLANDER | FALSE | ('210~002~AMPS~AI'+'210~003~AMPS~AI'+'210~004~AMPS~AI'+'210~005~AMPS~AI'+'210~006~AMPS~AI'+'210~007~AMPS~AI')*1.732*0.011 | 210~002~AMPS~AI | 210~003~AMPS~AI | 210~004~AMPS~AI | 210~005~AMPS~AI | 210~006~AMPS~AI | 210~007~AMPS~AI
BRCW2 | Braco West | 201 | 201 | BRACO GRID | TRUE | Brora Primary substation 2018-19 MW | PI tag1: 550~T1_T2~MW~AI
BRCW2 | Braco West | 201 | 208 | CRIEFF | FALSE | ('208~T1_T2_SU~AMPS~AI')*1.732*0.011 | PI tag1: 208~T1_T2_SU~AMPS~AI
BRCW2 | Braco West | 201 | 209 | DUNBLANE | FALSE | ('209~SUMM~AMPS~AI')*1.732*0.011 | PI tag1: 209~SUMM~AMPS~AI
BRCW2 | Braco West | 201 | 253 | FORTEVIOT | FALSE | ('253~TR1~MW~AI') | PI tag1: 253~TR1~MW~AI; PI tag2: 253~001~AMPS~AI; PI tag3: 253~TR1~AMPS~AI
BRCW2 | Braco West | 201 | 207 | GLENEAGLES | FALSE | ('207~T1_11~AMPS~AI'+'207~T2_11~AMPS~AI')*1.732*0.011 | PI tag1: 207~T1_11~AMPS~AI; PI tag2: 207~T2_11~AMPS~AI
BRCW2 | Braco West | 201 | 211 | KIPPEN | FALSE | ('211~11KV~AMPS~AI')*1.732*0.011 | PI tag1: 211~11KV~AMPS~AI
BRID | Bridge of Dun | 71 | 73 | BRECHIN | FALSE | ('073~TR1~MW~AI'+'073~TR2~MW~AI') | PI tag1: 073~TR1~MW~AI; PI tag2: 073~TR2~MW~AI
BRCW2 | Braco West | 290 | 290 | BRACO WEST GRID | TRUE | doesn’t exist in drawings
BRID | Bridge of Dun | 71 | 71 | BRIDGE OF DUN GRID | TRUE
BRID | Bridge of Dun | 71 | 72 | BRIDGE OF DUN 11kV | FALSE | ('072~T1_11~AMPS~AI')*1.732*0.011 | PI tag1: 072~T1_11~AMPS~AI
BRID | Bridge of Dun | 71 | 76 | INCHBARE | FALSE | ('076~TR1~AMPS~AI')*1.732*0.011 | PI tag1: 076~TR1~AMPS~AI
BRID | Bridge of Dun | 71 | 77 | LOGIE PERT | FALSE | ('077~TR1~MW~AI') | PI tag1: 077~TR1~MW~AI; PI tag2: 077~TR1~AMPS~AI
BRID | Bridge of Dun | 71 | 75 | MILL RD MONTROSE | FALSE | ('075~TR1~AMPS~AI')*1.732*0.011 | PI tag1: 075~TR1~AMPS~AI
BRID | Bridge of Dun | 71 | 74 | MONTROSE NORTH | FALSE | ('074~T1_T2_11~AMPS~AI')*1.732*0.011 | PI tag1: 074~T1_T2_11~AMPS~AI
BRID | Bridge of Dun | 71 | 952 | ST CYRUS | FALSE | ('952~common~AMPS~AI')*1.732*0.011 | 952~common~AMPS~AI | 952A~C01~MW~AI | 952D~C01~MW~AI | 952E~C01~AMPS~AI | 952F~C01~AMPS~AI
BRID | Bridge of Dun | 71 | 78 | x Use in T&C - CHECK DEPO | FALSE
BRID | Bridge of Dun | 71 | 278 | x Use in T&C - CHECK DEPO | FALSE
BRID | Bridge of Dun | 71 | 281 | x Use in T&C - CHECK DEPO | FALSE
BROA | Broadford | 627 | 624 | ACHINTEE | FALSE
BROA | Broadford | 627 | 637 | BROADFORD | FALSE | ('627~T1~MW~AI') | PI tag1: 627~T1~MW~AI
BROA | Broadford | 627 | 633 | KISHORNHILL | FALSE | ('633~011~AMPS~AI'+'633~012~AMPS~AI')*1.732*0.011 | PI tag1: 633~011~AMPS~AI; PI tag2: 633~012~AMPS~AI
BROA | Broadford | 627 | 627 | BROADFORD GRID | TRUE | [10 empty] | Kishorn Hill Primary substation 2018-19 | 633~1H0~AMPS~AI | 633~1H0~KV~AI
BROA | Broadford | 627 | 634 | KYLE | FALSE | ('634~T1_T2~AMPS~AI')*1.732*0.011 | PI tag1: 634~T1_T2~AMPS~AI
BROA | Broadford | 627 | 623 | LOWER OLLACH | FALSE | ('623~11KV~AMPS~AI')*1.732*0.011 | PI tag1: 623~11KV~AMPS~AI
BROA | Broadford | 627 | 636 | NOSTIE BRIDGE | FALSE | ('636~T1~AMPS~AI')*1.732*0.011 | PI tag1: 636~T1~AMPS~AI
BROA | Broadford | 627 | 641 | SHIELDAIG | FALSE | ('641~11KV~AMPS~AI')*1.732*0.011 | PI tag1: 641~11KV~AMPS~AI
BROA | Broadford | 627 | 639 | SKULAMUS | FALSE | ('639~T1~AMPS~AI')*1.732*0.011 | PI tag1: 639~T1~AMPS~AI
BROR | Brora | 510 | 524 | BENBRAGGIE MAST | FALSE | no PI tag
BROR | Brora | 510 | 510 | BRORA GRID | TRUE | Burghmuir Primary substation 2018-19 | PI tag1: 246~T1_T2_11~AMPS~AI
BROR | Brora | 510 | 550 | BRORA | FALSE | ('550~T1_T2~MW~AI') | PI tag1: 550~T1_T2~MW~AI
BROR | Brora | 510 | 557 | DORNOCH | FALSE | ('557~T1~AMPS~AI')*1.732*0.011 | PI tag1: 557~T1~AMPS~AI
BROR | Brora | 510 | 525 | GOLSPIE | FALSE | ('525~T1~MW~AI') | PI tag1: 525~T1~MW~AI
BROR | Brora | 510 | 560 | HELMSDALE | FALSE | ('560~TR1~MW~AI') | PI tag1: 560~TR1~MW~AI
BUMU | Burghmuir | 245 | 246 | BURGHMUIR | FALSE | ('246~T1_T2_11~AMPS~AI')*1.732*0.011 | PI tag1: 246~T1_T2_11~AMPS~AI
BUMU | Burghmuir | 245 | 245 | BURGHMUIR GRID | TRUE | Carnoustie Primary substation 2018-19
BUMU | Burghmuir | 245 | 249 | GOODLYBURN | FALSE | ('249~T1~MW~AI'+'249~T2~MW~AI') | PI tag1: 249~T1~MW~AI; PI tag2: 249~T2~MW~AI
BUMU | Burghmuir | 245 | 272 | NORTH MUIRTON | FALSE | ('272~SS_11~AMPS~AI')*1.732*0.011 | PI tag1: 272~SS_11~AMPS~AI
BUMU | Burghmuir | 245 | 270 | REDGORTON | FALSE | ('270~common~AMPS~AI')*1.732*0.011 | PI tag1: 270~common~AMPS~AI
BUMU | Burghmuir | 245 | 248 | THIMBLEROW | FALSE | ('248~002~AMPS~AI'+'248~003~AMPS~AI'+'248~005~AMPS~AI'+'248~006~AMPS~AI'+'248~007~AMPS~AI'+'248~008~AMPS~AI'+'248~009~AMPS~AI'+'248~010~AMPS~AI'+'248~011~AMPS~AI')*1.732*0.011 | 248~002~AMPS~AI | 248~003~AMPS~AI | 248~005~AMPS~AI | 248~006~AMPS~AI | 248~007~AMPS~AI | 248~008~AMPS~AI | 248~009~AMPS~AI | 248~010~AMPS~AI | 248~011~AMPS~AI
CAAD | Carradale | 302 | 372 | BALLIEKINE | FALSE | ('372~SS_LOAD~AMPS~AI')*1.732*0.011 | PI tag1: 372~SS_LOAD~AMPS~AI
CAAD | Carradale | 302 | 302 | CARRADALE GRID | TRUE | Coldbackie Primary substation 2018-19 | PI tag1: 581~11KV~AMPS~AI
CAAD | Carradale | 302 | 318 | BALLURE | FALSE | ('318~common~AMPS~AI')*1.732*0.011 | PI tag1: 318~common~AMPS~AI; PI tag2: 318A~C01~AMPS~AI; PI tag3: 318A~C01~MW~AI
CAAD | Carradale | 302 | 370 | BRODICK | FALSE | ('370~T1~MW~AI'+'370~T2~MW~AI') | PI tag1: 370~T1~MW~AI; PI tag2: 370~T2~MW~AI
CAAD | Carradale | 302 | 312 | CAMPBELTOWN | FALSE | ('312~TR1~MW~AI'+'312~TR2~MW~AI') | 312~TR1~MW~AI | 312~TR2~MW~AI | 312~TRANS~AMPS~AI | LUSSA~G2~MW~AI | LUSSA~G1~MW~AI
CAAD | Carradale | 302 | 338 | CLAONAIG | FALSE | No PI tag
CAAD | Carradale | 302 | 336 | DIPPEN | FALSE | No PI tag
CAAD | Carradale | 302 | 373 | MACHRIE | FALSE | ('373~011~AMPS~AI')*1.732*0.011 | PI tag1: 373~011~AMPS~AI
CAAD | Carradale | 302 | 349 | WESTPARK FERGUS | FALSE | ('349~11KV_LOAD~AMPS~AI')*1.732*0.011 | PI tag1: 349~11KV_LOAD~AMPS~AI
CAAD | Carradale | 302 | 371 | WHITING BAY | FALSE | ('371~T1_11KV~AMPS~AI')*1.732*0.011 | PI tag1: 371~T1_11KV~AMPS~AI
CASS | Cassley | 512 | 511 | CANNICH | FALSE | Not a primary sub
CASS | Cassley | 512 | 563 | OVERSCAIG | FALSE | No PI tag
CASS | Cassley | 512 | 512 | CASSLEY GRID | TRUE | Craigton Primary substation 2018-19 | PI tag1: CRAI~CBL1~AMPS~AI
CASS | Cassley | 512 | 544 | RHICONICH | FALSE | ('544~T1_T2~AMPS~AI')*1.732*0.011 | PI tag1: 544~T1_T2~AMPS~AI
CHAR | Charleston | 001 | 005 | BUTTARS LOAN | FALSE | only a normaly open point
CEAN | Ceannacroc | 711 | 711 | CEANNACROC GRID | TRUE | Cromalt Primary substation 2018-19 (MW Tags) | PI tag1: 326~TR1~MW~AI
CHAR | Charleston | 001 | 001 | CHARLESTON GRID | TRUE | Crosshills Primary substation 2018-19 | PI tag1: 551~T1_T2~AMPS~AI
CHAR | Charleston | 001 | 002 | CHARLESTON | FALSE | ('002~TR1~MW~AI'+'002~TR2~MW~AI')*1.732*0.011 | PI tag1: 002~TR1~MW~AI; PI tag2: 002~TR2~MW~AI
CHAR | Charleston | 001 | 004 | GOURDIE | FALSE | ('004~TR1~MW~AI') | PI tag1: 004~TR1~MW~AI; PI tag2: 004~TR1~AMPS~AI
CHAR | Charleston | 001 | 003 | MENZIESHILL | FALSE | ('003~TR1~MW~AI'+'003~TR2~MW~AI') | 003~TR1~MW~AI | 003~TR2~MW~AI | 002~003~AMPS~AI | 003~001~AMPS~AI | 003~002~AMPS~AI | 003~003~AMPS~AI | 003~004~AMPS~AI | 003~005~AMPS~AI
CHAR | Charleston | 001 | 006 | NINEWELLS | FALSE | ('006~004~AMPS~AI')*1.732*0.011 | PI tag1: 006~004~AMPS~AI
CLAC | Clachan | 311 | 387 | BUTTERBRIDGE | FALSE | no PI tag
CLAC | Clachan | 311 | 311 | CLACHAN GRID | TRUE
CLAC | Clachan | 311 | 388 | DOUGLAS PIER | FALSE | ('388~TRANS~AMPS~AI')*1.732*0.011 | PI tag1: 388~TRANS~AMPS~AI
CLAC | Clachan | 311 | 321 | INVERARAY | FALSE | ('321~TR1~MW~AI') | PI tag1: 321~TR1~MW~AI
CLAC | Clachan | 311 | 369 | LOCHGOILHEAD | FALSE | ('369~T1~AMPS~AI')*1.732*0.011 | PI tag1: 369~T1~AMPS~AI; PI tag2: 369A~C01~AMPS~AI; PI tag3: 369~SS~AMPS~AI
CLAC | Clachan | 311 | 382 | STRACHUR | FALSE | ('382~11KV~AMPS~AI')*1.732*0.011 | PI tag1: 382~11KV~AMPS~AI
CLAY | Clayhills | 823 | 808 | BALNAGASK | FALSE | ('CLAY~6L5~AMPS~AI')*1.732*0.011 | PI tag1: CLAY~6L5~AMPS~AI
CLAY | Clayhills | 823 | 826 | CLAYHILLS | FALSE | ('CLAY~4L5~AMPS~AI'+'CLAY~5L5~AMPS~AI')*1.732*0.011 | PI tag1: CLAY~4L5~AMPS~AI; PI tag2: CLAY~5L5~AMPS~AI
CLAY | Clayhills | 823 | 823 | CLAYHILLS GRID | TRUE | Denburn Primary substation 2018-19 - | PI tag1: WIOW~8L5_FEED~AMPS~AI; PI tag2: 841~T1~Amps~ai; PI tag3: 841~T2~Amps~ai; PI tag4: 841~common~volts~ai |  | Clayhills Primary substation 2018-19 | CLAY~4L5~AMPS~AI | CLAY~5L5~AMPS~AI
CLAY | Clayhills | 823 | 827 | COMMERCE STREET | FALSE | ('827~TR1~MW~AI'+'827~TR2~MW~AI') | PI tag1: 827~TR1~MW~AI; PI tag2: 827~TR2~MW~AI
CLAY | Clayhills | 823 | 832 | CRAIGINCHES | FALSE | ('832~TR1~MW~AI'+'832~TR2~MW~AI') | PI tag1: 832~TR1~MW~AI; PI tag2: 832~TR2~MW~AI
COUA | Coupar Angus | 243 | 258 | ALYTH | FALSE | ('258~011~AMPS~AI')*1.732*0.011 | PI tag1: 258~011~AMPS~AI
COUA | Coupar Angus | 243 | 257 | BLAIRGOWRIE | FALSE | ('257~SUMM~AMPS~AI')*1.732*0.011 | PI tag1: 257~SUMM~AMPS~AI
COUA | Coupar Angus | 243 | 243 | COUPAR ANGUS GRID | TRUE | [10 empty] | Blairgowrie Primary substation 2018-19 | 257~SUMM~AMPS~AI | 257~BBAR~KV~AI
COUA | Coupar Angus | 243 | 256 | CAPUTH | FALSE | ('256~T1~MW~AI'+'256~T2~MW~AI') | PI tag1: 256~T1~MW~AI; PI tag2: 256~T2~MW~AI
COUA | Coupar Angus | 243 | 244 | COUPAR ANGUS | FALSE | ('244~001~AMPS~AI'+'244~002~AMPS~AI'+'244~003~AMPS~AI'+'244~004~AMPS~AI')*1.732*0.011 | PI tag1: 244~001~AMPS~AI; PI tag2: 244~002~AMPS~AI; PI tag3: 244~003~AMPS~AI; PI tag4: 244~004~AMPS~AI
COUA | Coupar Angus | 243 | 259 | DALRULZION | FALSE | ('259~T1~AMPS~AI'+'259~T2~AMPS~AI')*1.732*0.011 | PI tag1: 259~T1~AMPS~AI; PI tag2: 259~T2~AMPS~AI
COUA | Coupar Angus | 243 | 90 | LEOCH | FALSE | ('090~TR1~MW~AI') | 090~TR1~MW~AI | 090B~C01~MW~AI | 090A~C01~MW~AI | 090D~C01~AMPS~AI | 090C~C01~MW~AI
CRAI | Craigiebuckler | 829 | 830 | CRAIGIEBUCKLER | FALSE | ('CRAI~CBL1~AMPS~AI'+'CRAI~CBL2~AMPS~AI')*1.732*0.033 | PI tag1: CRAI~CBL1~AMPS~AI; PI tag2: CRAI~CBL2~AMPS~AI
CRAI | Craigiebuckler | 829 | 829 | CRAIGIEBUCKLER GRID | TRUE | Drymen Primary substation 2018-19_completed | PI tag1: 203~T1~AMPS~AI; PI tag2: 203~BUSBAR~KV~AI; PI tag3: 203A~C01~MW~AI
CRAI | Craigiebuckler | 829 | 834 | CRAIGTON | FALSE | No PI available
CRAI | Craigiebuckler | 829 | 836 | CULTER | FALSE | ('836~TR1~MW~AI'+'836~TR2~MW~AI') | PI tag1: 836~TR1~MW~AI; PI tag2: 836~TR2~MW~AI
CRAI | Craigiebuckler | 829 | 939 | RUTHRIESTON | FALSE | ('CRAI~QLN2~AMPS~AI')*1.732*0.011 | PI tag1: CRAI~QLN2~AMPS~AI
DUDH | Dudhope | 31 | 32 | CONSTABLE STREET | FALSE | ('032~TR1~MW~AI'+'032~TR2~MW~AI') | 032~TR1~MW~AI | 032~TR2~MW~AI | 032~001~AMPS~AI | 032~002~AMPS~AI | 032~003~AMPS~AI | 032~004~AMPS~AI | 032~005~AMPS~AI | 032~006~AMPS~AI
DAAS | Dallas | 473 | 473 | DALLAS | TRUE
DOUN1 | Dounreay | 598 | 598 | DOUNREAY | TRUE
DUDH | Dudhope | 31 | 31 | DUDHOPE GRID | TRUE
DUDH | Dudhope | 31 | 595 | DUNBEATH GRID | FALSE | No PI tag
DUDH | Dudhope | 31 | 33 | ROSEBANK STREET | FALSE | ('033~TR1~AMPS~AI')*1.732*0.011 | PI tag1: 033~TR1~AMPS~AI
DUGR | Dungervan | 638 | 629 | DRYNOCH | FALSE | ('629~T1~AMPS~AI')*1.732*0.011 | PI tag1: 629~T1~AMPS~AI; PI tag2: 629~011~AMPS~AI; PI tag3: 629~012~AMPS~AI
DUGR | Dungervan | 638 | 632 | PORTREE | FALSE | ('632~T1~AMPS~AI'+'632~T2~AMPS~AI')*1.732*0.011 | PI tag1: 632~T1~AMPS~AI; PI tag2: 632~T2~AMPS~AI
DUGR | Dungervan | 638 | 640 | UIG | FALSE | ('640~11KV~AMPS~AI')*1.732*0.011 | PI tag1: 640~11KV~AMPS~AI; PI tag2: 640~011~AMPS~AI; PI tag3: 640~012~AMPS~AI
DUGR | Dungervan | 638 | 638 | DUNVEGAN GRID | TRUE | [10 empty] | Portree Primary 2018-19 | 632~T1~AMPS~AI
DUNO | Dunoon | 380 | 376 | ARDYNE POINT | FALSE | No PI tag
DUNO | Dunoon | 380 | 365 | BRUCHAG | FALSE | ('365~TR1~MW~AI'+'365~TR2~MW~AI') | PI tag1: 365~TR1~MW~AI; PI tag2: 365~TR2~MW~AI
DUNO | Dunoon | 380 | 385 | COLINTRAIVE | FALSE | No PI tag
DUNO | Dunoon | 380 | 363 | DUNOON | FALSE | ('363~SUMM~AMPS~AI')*1.732*0.011 | PI tag1: 363~SUMM~AMPS~AI
DUNO | Dunoon | 380 | 383 | GLENDARUEL | FALSE | No PI tag
DUNO | Dunoon | 380 | 379 | INNELLAN | FALSE | ('379~SUMM~AMPS~AI')*1.732*0.011 | PI tag1: 379~SUMM~AMPS~AI; PI tag2: 379~002~AMPS~AI; PI tag3: 379~003~AMPS~AI; PI tag4: 379~005~AMPS~AI
DUNO | Dunoon | 380 | 366 | KAMES | FALSE | ('366~11KV_SS~AMPS~AI')*1.732*0.011 | PI tag1: 366~11KV_SS~AMPS~AI
DUNO | Dunoon | 380 | 384 | NEWTON | FALSE | No PI tag
DUNO | Dunoon | 380 | 375 | OTTER FERRY | FALSE | ('375~11KV_SS~AMPS~AI')*1.732*0.011 | PI tag1: 375~11KV_SS~AMPS~AI
DUNO | Dunoon | 380 | 380 | DUNOON GRID | TRUE | Edzell Primary substation 2018-19_completed | PI tag1: 847~common~AMPS~AI; PI tag2: 847A_C01_AMPSn
DUNO | Dunoon | 380 | 362 | ROTHESAY | FALSE | ('362~T1_T2~AMPS~AI')*1.732*0.011 | PI tag1: 362~T1_T2~AMPS~AI
DUNO | Dunoon | 380 | 364 | SANDBANK | FALSE | ('364~002~AMPS~AI'+'364~003~AMPS~AI'+'364~004~AMPS~AI'+'364~005~AMPS~AI')*1.732*0.011 | PI tag1: 364~002~AMPS~AI; PI tag2: 364~003~AMPS~AI; PI tag3: 364~004~AMPS~AI; PI tag4: 364~005~AMPS~AI
DYCE | Dyce | 843 | 807 | BALMEDIE | FALSE | ('807~common~AMPS~AI')*1.732*0.011 | PI tag1: 807~common~AMPS~AI
DYCE | Dyce | 843 | 844 | DYCE NORTH | FALSE | ('843~1L5~MW~AI'+'843~2L5~MW~AI') | PI tag1: 843~1L5~MW~AI; PI tag2: 843~2L5~MW~AI
DYCE | Dyce | 843 | 843 | DYCE GRID | TRUE | Errol Primary substation 2018-19_completed | PI tag1: 254~SUMM~AMPS~AI; PI tag2: 254~SS~KV~AI; PI tag3: 254A~C01~AMPS~AI |  | Dyce North Primary substation 2018-19 MW_completed
DYCE | Dyce | 843 | 849 | ELLON 11 kV | FALSE | ('849A~TR1~AMPS~AI'+'849A~TR2~AMPS~AI')*1.732*0.011 | PI tag1: 849A~TR1~AMPS~AI; PI tag2: 849A~TR2~AMPS~AI; PI tag3: 849~common~AMPS~AI
DYCE | Dyce | 843 | 884 | KINGSEAT | FALSE | ('884~common~AMPS~AI')*1.732*0.011 | PI tag1: 884~common~AMPS~AI; PI tag2: 884B~C01~AMPS~AI
ELGI | Elgin | 456 | 458 | ASHGROVE | FALSE | ('458~T1_T2~AMPS~AI')*1.732*0.011 | PI tag1: 458~T1_T2~AMPS~AI
EDIN | Edinbane | 355 | 355 | EDINBANE GRID | TRUE | Fochabers Primary substation 2018-19_completed | PI tag1: 487~11KV~AMPS~AI |  | Stoneywood T3 Primary substation 2018-19 | 947~TR3~MW~AI
ELGI | Elgin | 456 | 499 | BILBOHALL | FALSE | ('499~T1_T2~AMPS~AI')*1.732*0.011 | PI tag1: 499~T1_T2~AMPS~AI
ELGI | Elgin | 456 | 454 | BURGHEAD | FALSE | ('454~T1_T2~AMPS~AI')*1.732*0.011 | PI tag1: 454~T1_T2~AMPS~AI
ELGI | Elgin | 456 | 457 | CUMMING STREET | FALSE | ('457~T1_T2~AMPS~AI')*1.732*0.011 | PI tag1: 457~T1_T2~AMPS~AI
ELGI | Elgin | 456 | 456 | ELGIN GRID | TRUE | Foyers Primary substation 2018-19_completed | PI tag1: 718~T1~AMPS~AI |  | Cumming Street Primary substation 2018-19 | 457~T1_T2~AMPS~AI
ELGI | Elgin | 456 | 482 | ELGIN | FALSE | ('482~T1_T2~AMPS~AI')*1.732*0.011 | PI tag1: 482~T1_T2~AMPS~AI
ELGI | Elgin | 456 | 487 | FOCHABERS | FALSE | ('487~11KV~AMPS~AI')*1.732*0.011 | PI tag1: 487~11KV~AMPS~AI
ELGI | Elgin | 456 | 453 | KINLOSS | FALSE | ('453~T1_T2~AMPS~AI')*1.732*0.011 | PI tag1: 453~T1_T2~AMPS~AI
ELGI | Elgin | 456 | 488 | LHANBRYDE | FALSE | ('488~T1_T2~AMPS~AI')*1.732*0.011 | PI tag1: 488~T1_T2~AMPS~AI
ELGI | Elgin | 456 | 455 | LOSSIEMOUTH | FALSE | ('455~T1_T2~AMPS~AI')*1.732*0.011 | PI tag1: 455~T1_T2~AMPS~AI
FASN | Fasnakyle | 521 | 519 | FASNAKYLE PRIMARY | FALSE | ('FASN~T5~AMPS~AI')*1.732*0.011 | PI tag1: FASN~T5~AMPS~AI
FIDD | Fiddes | 851 | 847 | EDZELL | FALSE | ('847~common~AMPS~AI')*1.732*0.011 | PI tag1: 847~common~AMPS~AI; PI tag2: 847A_C01_AMPSn
FASN | Fasnakyle | 521 | 521 | FASNAKYLE GRID | TRUE
FIDD | Fiddes | 851 | 873 | INVERBERVIE | FALSE | ('873~TR1~MW~AI'+'873~TR2~MW~AI') | PI tag1: 873~TR1~MW~AI; PI tag2: 873~TR2~MW~AI
FIDD | Fiddes | 851 | 890 | LAURENCEKIRK | FALSE | ('890~TR1~MW~AI'+'890~TR2~MW~AI') | PI tag1: 890~TR1~MW~AI; PI tag2: 890~TR2~MW~AI
FIDD | Fiddes | 851 | 945 | STONEHAVEN | FALSE | ('945~T1~AMPS~AI'+'945~T2~AMPS~AI')*1.732*0.011 | 945~T1~AMPS~AI | 945~T2~AMPS~AI | 945B~C01~AMPS~AI | 945C~C01~AMPS~AI | 890A~C01~MW~AI
FAUG | Fort Augustus | 716 | 710 | ABERCHALDER | FALSE | No PI tag
FAUG | Fort Augustus | 716 | 716 | FORT AUGUSTUS GRID | TRUE | Glencoe Primary substation 2018-19_completed | 330~001~AMPS~AI | 729~2L5~AMPS~AI | 330~001~AMPS~AI | 330~001~KV~AI | 330~001~MVAR~AI | 330~001~MW~AI
FAUG | Fort Augustus | 716 | 745 | BUNOICH | FALSE | ('745~011~AMPS~AI')*1.732*0.011 | PI tag1: 745~011~AMPS~AI
FAUG | Fort Augustus | 716 | 517 | DRUMNADROCHIT | FALSE | ('517~TR1~AMPS~AI')*1.732*0.011 | PI tag1: 517~TR1~AMPS~AI; PI tag2: 517A~C01~AMPS~AI
FAUG | Fort Augustus | 716 | 709 | FARR GRID | FALSE | No PI tag
FAUG | Fort Augustus | 716 | 396 | GLEN LAOGH | FALSE | No PI tag
FETT | Fetteresso | 989 | 989 | FETTERSSO GRID | TRUE | Gleneagles Primary substation 2018-19_completed
FAUG | Fort Augustus | 716 | 781 | GLENDOE PRIMARY | FALSE | ('781~002~AMPS~AI'+'781~003~AMPS~AI')*1.732*0.011 | PI tag1: 781~002~AMPS~AI; PI tag2: 781~003~AMPS~AI
FIDD | Fiddes | 851 | 851 | FIDDES | TRUE | [10 empty] | Inverbervie Primary substation 2018-19 (MW Tags) | 873~TR1~MW~AI | 873~TR2~MW~AI
FAUG | Fort Augustus | 716 | 766 | INVERGARRY | FALSE | No PI tag
FAUG | Fort Augustus | 716 | 742 | MARKETHILL | FALSE | ('742~011~AMPS~AI')*1.732*0.011 | PI tag1: 742~011~AMPS~AI
FAUG | Fort Augustus Grid | 716 | 748 | QUOICH PRIMARY | FALSE | ('748~1L5~MW~AI') | PI tag1: 748~1L5~MW~AI
FWIL | Fort William | 715 | 702 | ANNAT | FALSE | ('702~TR1~MW~AI') | PI tag1: 702~TR1~MW~AI
FRAS | Fraserburgh | 853 | 853 | FRASERBURGH GRID | TRUE | Goodlyburn Primary substation 2018-19_completed | PI tag1: 249~T1~MW~AI; PI tag2: 249~T2~MW~AI
FWIL | Fort William | 715 | 740 | ARISAIG | FALSE | ('740~T1~AMPS~AI')*1.732*0.011 | PI tag1: 740~T1~AMPS~AI
FWIL | Fort William | 715 | 782 | CARNOCH REGULATOR | FALSE | it is not a primary | PI tag1: 782~33KV~AMPS~AI
FWIL | Fort William | 715 | 744 | CORRAN | FALSE | ('744~11KV~AMPS~AI')*1.732*0.011 | PI tag1: 744~11KV~AMPS~AI
FWIL | Fort William | 715 | 720 | DAILBEG | FALSE | No PI tag
FWIL | Fort William | 715 | 715 | FORT WILLIAM GRID | TRUE | [10 empty] | Glensanda Primary substation 2018-19_completed | 714~common~AMPS~AI | 714~common~AMPS~AI
FWIL | Fort William | 715 | 395 | FISHNISH | FALSE | No PI tag
FWIL | Fort William | 715 | 714 | GLENSANDA | FALSE | ('714~common~AMPS~AI')*1.732*0.011 | PI tag1: 714~common~AMPS~AI
FWIL | Fort William | 715 | 756 | GLENUIG | FALSE | No PI tag
FWIL | Fort William | 715 | 724 | INVERLOCHY | FALSE | ('724~TR1~MW~AI'+'724~TR2~MW~AI') | PI tag1: 724~TR1~MW~AI; PI tag2: 724~TR2~MW~AI; PI tag3: 724C~C01~AMPS~AI; PI tag4: MUCO~G1~MW~AI
FWIL | Fort William | 715 | 771 | KINGAIRLOCH | FALSE | No PI tag
FWIL | Fort William | 715 | 754 | KINLOCHMOIDART | FALSE | No PI tag
FWIL | Fort William | 715 | 721 | LIDDESDALE | FALSE | ('721~016~AMPS~AI')*1.732*0.011 | PI tag1: 721~016~AMPS~AI
FWIL | Fort William | 715 | 730 | LOCHAILORT REGULATOR | FALSE | it is not a primary | PI tag1: 730~REG1~AMPS~AI
FWIL | Fort William | 715 | 747 | LOCHALINE | FALSE | ('747~T1_33KV~AMPS~AI')*1.732*0.033 | PI tag1: 747~T1_33KV~AMPS~AI; PI tag2: 747~MULLLOAD~33AMPS~AI
FWIL | Fort William | 715 | 731 | MALLAIG | FALSE | ('731~TR1~AMPS~AI')*1.732*0.011 | PI tag1: 731~TR1~AMPS~AI
FWIL | Fort William | 715 | 734 | PINEGROVE | FALSE | ('734~T1_T2~AMPS~AI')*1.732*0.011 | PI tag1: 734~T1_T2~AMPS~AI
FWIL | Fort William | 715 | 753 | POOR HOUSE | FALSE | No PI tag
FWIL | Fort William | 715 | 732 | RAHOY | FALSE | No PI tag
FWIL | Fort William | 715 | 749 | SALEN 2 | FALSE | ('749~T1~AMPS~AI')*1.732*0.011 | PI tag1: 749~T1~AMPS~AI
FWIL | Fort William | 715 | 755 | SHONA BEAG | FALSE | No PI tag
FWIL | Fort William | 715 | 751 | STRONTIAN | FALSE | ('751~11KV~AMPS~AI')*1.732*0.011 | PI tag1: 751~11KV~AMPS~AI
FRAS | Fraserburgh | 853 | 821 | CAIRNBULG | FALSE | No PI tag
FRAS | Fraserburgh | 853 | 854 | FRASERBURGH | FALSE | ('854~TR1~MW~AI'+'854~TR3~MW~AI') | PI tag1: 854~TR1~MW~AI; PI tag2: 854~TR3~MW~AI; PI tag3: 854A~C01~MW~AI
GLAG | Glenagnes | 21 | 21 | GLENAGNES GRID | TRUE | Invergordon Primary substation 2018-19 (11kV DG) | PI tag1: 559~T1_T2~AMPS~AI; PI tag2: 559A~001~MW~AI; PI tag3: 559A~002~MW~AI
GLAG | Glenagnes | 21 | 24 | OVERGATE | FALSE | ('024~TR1~AMPS~AI')*1.732*0.011 | PI tag1: 024~TR1~AMPS~AI
GLAG | Glenagnes | 21 | 25 | WALTON | FALSE | ('025~T2_T3_11~AMPS~AI')*1.732*0.011 | PI tag1: 025~T2_T3_11~AMPS~AI
GRUB | Grudie Bridge | 526 | 505 | ACHILTIBUIE | FALSE | ('505~T1_11~AMPS~AI')*1.732*0.011 | PI tag1: 505~T1_11~AMPS~AI; PI tag2: 505B~C01~MW~AI; PI tag3: 505C~C01~AMPS~AI; PI tag4: 505B~C01~AMPS~AI
GRUB | Grudie Bridge | 526 | 798 | ACHNASHEEN | FALSE | its not a primary but regulator
GRUB | Grudie Bridge | 526 | 504 | AULTBEA | FALSE | ('504~T1~MW~AI') | PI tag1: 504~T1~MW~AI
GRUB | Grudie Bridge | 526 | 535 | BIDEN CLAN RAONAILD | FALSE | No PI tag
GRUB | Grudie Bridge | 526 | 562 | COMRIE | FALSE | No PI tag
GRUB | Grudie Bridge | 526 | 526 | GRUDIE BRIDGE | TRUE | Kames Primary substation 2018-19 | PI tag1: 366~11KV_SS~AMPS~AI; PI tag2: 366~11KV_SS~AMPS~AI; PI tag3: 366~11KV_SS~KV~AI
GRUB | Grudie Bridge | 526 | 514 | CONON FALLS | FALSE | ('J757R~COMMON~AMPS~AI')*1.732*0.011 | PI tag1: J757R~COMMON~AMPS~AI
GRUB | Grudie Bridge | 526 | 573 | CUILEIG POWER STATION | FALSE | No PI tag
GRUB | Grudie Bridge | 526 | 518 | DRUMRUNIE | FALSE | No PI tag
GRUB | Grudie Bridge | 526 | 567 | GARBAT FOREST | FALSE | No PI tag
GRUB | Grudie Bridge | 526 | 569 | GARVE | FALSE | Not a primary sub
GRUB | Grudie Bridge | 526 | 527 | INVERBROOM | FALSE | No PI tag
GRUB | Grudie Bridge | 526 | 531 | KERRY FALLS | FALSE | ('531~080~AMPS~AI')*1.732*0.011 | PI tag1: 531~080~AMPS~AI; PI tag2: 531B~C01~AMPS~AI
GRUB | Grudie Bridge | 526 | 532 | KINLOCHEWE | FALSE | No PI tag
GRUB | Grudie Bridge | 526 | 507 | LETTEREWE | FALSE | No PI tag
GRUB | Grudie Bridge | 526 | 799 | LOCH DUBH P S | FALSE | No PI tag
GRUB | Grudie Bridge | 526 | 568 | LOCH GLASCARNOCH | FALSE | No PI tag
GRUB | Grudie Bridge | 526 | 556 | LOCHINVER | FALSE | ('556~T1~MW~AI') | PI tag1: 556~T1~MW~AI; PI tag2: 556~011~AMPS~AI; PI tag3: 556~T1~POWER~AI; PI tag4: 556~011~AMPS~AI
GRUB | Grudie Bridge | 526 | 564 | MINOR GRUDIE | FALSE | No PI tag
GRUB | Grudie Bridge | 526 | 549 | ULLAPOOL | FALSE | ('549~071~AMPS~AI'+'549~072~AMPS~AI')*1.732*0.011 | PI tag1: 549~071~AMPS~AI; PI tag2: 549~072~AMPS~AI
INNE | Inverness | 725 | 712 | CULLODEN | FALSE | ('712~T1~AMPS~AI'+'712~T2~AMPS~AI')*1.732*0.011 | PI tag1: 712~T1~AMPS~AI; PI tag2: 712~T2~AMPS~AI
INNE | Inverness | 725 | 713 | DALNEIGH | FALSE | ('713~T1_T2~AMPS~AI')*1.732*0.011 | PI tag1: 713~T1_T2~AMPS~AI
INNE | Inverness | 725 | 725 | INVERNESS GRID | TRUE | Kinloch Primary substation 2018-19 | 333~T1~MW~AI | 333~PEAK~PERCENT~AI | 333~T1~AMPS~AI | 333~T1~KV~AI | 333~T1~MVAR~AI | 333~T1~MW~AI |  |  |  | Hilton Primary substation 2018-19_completed | 750~T1_T2~AMPS~AI
INNE | Inverness | 725 | 761 | ERROGIE | FALSE | No PI tag
INNE | Inverness | 725 | 718 | FOYERS | FALSE | ('718~T1~AMPS~AI')*1.732*0.011 | PI tag1: 718~T1~AMPS~AI
INNE | Inverness | 725 | 750 | HILTON | FALSE | ('750~T1_T2~AMPS~AI')*1.732*0.011 | PI tag1: 750~T1_T2~AMPS~AI
INNE | Inverness | 725 | 757 | INVERARNIE | FALSE | ('757~011~AMPS~AI')*1.732*0.011 | PI tag1: 757~011~AMPS~AI
INNE | Inverness | 725 | 726 | INVERNESS 11 kV | FALSE | ('725~T1_T2~AMPS~AI')*1.732*0.011 | PI tag1: 725~T1_T2~AMPS~AI
INNE | Inverness | 725 | 735 | RAIGMORE | FALSE | ('735~014~AMPS~AI')*1.732*0.011 | PI tag1: 735~014~AMPS~AI
INNE | Inverness | 725 | 741 | WATERLOO PLACE | FALSE | ('741~T1_T2~AMPS~AI')*1.732*0.011 | PI tag1: 741~T1_T2~AMPS~AI
INNE | Inverness | 725 | 763 | WESTER DRUMMOND | FALSE | No PI tag
MACD | Macduff | 405 | 405 | MACDUFF | TRUE | Kishorn Hill Primary substation 2018-19 | PI tag1: 633~1H0~AMPS~AI; PI tag2: 633~1H0~KV~AI |  | Buckie Primary substation 2018-19 (11kV DG) | 462~T1_T2~AMPS~AI | 462A~CO1~MW~AI
KEIT | Keith | 463 | 460 | ABERLOUR | FALSE | ('460~T1_T2~AMPS~AI')*1.732*0.011 | PI tag1: 460~T1_T2~AMPS~AI
KEIT | Keith | 463 | 462 | BUCKIE | FALSE | ('462~T1_T2~AMPS~AI')*1.732*0.011 | PI tag1: 462~T1_T2~AMPS~AI; PI tag2: 462A~CO1~MW~AI
KEIT | Keith | 463 | 469 | CULLEN | FALSE | ('469~TR1~MW~AI') | PI tag1: 469~TR1~MW~AI
KEIT | Keith | 463 | 461 | DUFFTOWN | FALSE | ('461~T1_T2~AMPS~AI'+'461~T1_T2~AMPS~AI')*1.732*0.011 | PI tag1: 461~T1_T2~AMPS~AI; PI tag2: 461~T1_T2~AMPS~AI
KEIT | Keith | 463 | 869 | HUNTLY | FALSE | ('869~common~AMPS~AI')*1.732*0.011 | PI tag1: 869~common~AMPS~AI
KEIT | Keith | 463 | 871 | INSCH | FALSE | ('871~common~AMPS~AI')*1.732*0.011 | PI tag1: 871~common~AMPS~AI
KEIT | Keith | 463 | 463 | KEITH GRID | TRUE | Leoch Primary substation 2018-19 (11kV DG) | 090~TR1~MW~AI | 090B~C01~MW~AI | 090A~C01~MW~AI | 090D~C01~AMPS~AI | 090D~C01~KV~AI | 090C~C01~MW~AI |  |  |  | Limehillocks Primary substation 2018-19 (11kV DG) | 465~11KV~AMPS~AI | 465A~C01~AMPS~AI | 465A~C01~KV~AI | 465A~C01~MW~AI
KEIT | Keith | 463 | 464 | KEITH | FALSE | ('463~T1~AMPS~AI'+'463~T2~AMPS~AI')*1.732*0.011 | PI tag1: 463~T1~AMPS~AI; PI tag2: 463~T2~AMPS~AI
KEIT | Keith | 463 | 465 | LIMEHILLOCKS | FALSE | ('465~013~AMPS~AI'+'465~014~AMPS~AI'+'465~015~AMPS~AI')*1.732*0.011 | PI tag1: 465~013~AMPS~AI; PI tag2: 465~014~AMPS~AI; PI tag3: 465~015~AMPS~AI
KEIT | Keith | 463 | 401 | MARNOCH | FALSE | ('401~T1_T2~AMPS~AI')*1.732*0.011 | PI tag1: 401~T1_T2~AMPS~AI
KEIT | Keith | 463 | 435 | PORTSOY | FALSE | ('435~TR2~AMPS~AI')*1.732*0.011 | PI tag1: 435~TR2~AMPS~AI
KEIT | Keith | 463 | 459 | ROTHES | FALSE | ('459~T1_T2~AMPS~AI')*1.732*0.011 | PI tag1: 459~T1_T2~AMPS~AI
KEIT | Keith | 463 | 964 | TURRIFF | FALSE | ('964E~C01~MW~AI'+'964F~C01~MW~AI'+'964G~C01~MW~AI') | 964E~C01~MW~AI | 964F~C01~MW~AI | 964G~C01~MW~AI | 964H~C01~AMPS~AI |  | 964J~C01~MW~AI | 964K~C01~AMPS~AI
KIIN | Killin | 214 | 214 | KILLIN GRID | TRUE | Limehillocks Primary substation 2018-19 (11kV DG) | PI tag1: 465~11KV~AMPS~AI; PI tag2: 465A~C01~AMPS~AI; PI tag3: 465A~C01~KV~AI; PI tag4: 465A~C01~MW~AI
KIIN | Killin | 214 | 269 | CASHLIE | FALSE | No PI tag
KIIN | Killin | 214 | 219 | KILLIN TOWN | FALSE | ('219~011~AMPS~AI')*1.732*0.011 | PI tag1: 219~011~AMPS~AI
KIIN | Killin | 214 | 217 | LOCHEARNHEAD | FALSE | ('217~common~AMPS~AI')*1.732*0.011 | PI tag1: 217~common~AMPS~AI; PI tag2: 217A~C01~AMPS~AI; PI tag3: 217A~C01~MW~AI; PI tag4: 217D~C01~AMPS~AI
KIIN | Killin | 214 | 221 | LUBNAIG | FALSE | No PI tag
KILO | Kinlochleven | 729 | 330 | GLENCOE | FALSE | ('330~001~MW~AI') | PI tag1: 330~001~MW~AI; PI tag2: 729~2L5~AMPS~AI; PI tag3: 330~001~AMPS~AI
KILO | Kinlochleven | 729 | 729 | KINLOCHLEVEN | TRUE | [10 empty] | Kinlochleven Primary substation 2018-19 | 729~T1~MW~AI | 729~T2~MW~AI
KINT | Kintore | 887 | 810 | BANCHORY | FALSE | ('810~T1~MW~AI'+'810~T2~MW~AI') | PI tag1: 810~T1~MW~AI; PI tag2: 810~T2~MW~AI
KINT | Kintore | 887 | 856 | FYVIE | FALSE | ('856~T1~MW~AI') | 856~T1~MW~AI | 856C~C01~AMPS~AI | 856A~C01~MW~AI | 856B~C01~AMPS~AI | 903B~C01~AMPS~AI | 856~T2~MW~AI | 856~009~AMPS~AI | 856D~C01~AMPS~AI | 856E~C01~AMPS~AI
KINT | Kintore | 887 | 875 | INVERURIE | FALSE | ('875~T1~MW~AI'+'875~T2~MW~AI'+'875~TR3~MW~AI') | 875~T1~MW~AI | 875~T2~MW~AI | 875~TR3~MW~AI | 875A~C01~MW~AI | 875B~C01~MW~AI
KINT | Kintore | 887 | 881 | KEMNAY | FALSE | ('881~common~AMPS~AI')*1.732*0.011 | PI tag1: 881~common~AMPS~AI
KINT | Kintore | 887 | 886 | KINTORE SUPERGRID | FALSE | No PI tag
KINT | Kintore | 887 | 887 | KINTORE GRID | TRUE | Lochgoilhead Primary substation 2018-19 | PI tag1: 369~SS~AMPS~AI; PI tag2: 369A~C01~AMPS~AI; PI tag3: 369A~C01~KV~AI; PI tag4: 369~T1~AMPS~AI |  | Midmar Primary substation 2018-19 | 907~T1~AMPS~AI
KINT | Kintore | 887 | 903 | METHLICK | FALSE | ('903~TOTAL~AMPS~AI')*1.732*0.011 | PI tag1: 903~TOTAL~AMPS~AI
KINT | Kintore | 887 | 907 | MIDMAR | FALSE | ('907~T1~AMPS~AI')*1.732*0.011 | PI tag1: 907~T1~AMPS~AI
KINT | Kintore | 887 | 921 | OLDMELDRUM | FALSE | ('921~common~AMPS~AI')*1.732*0.011 | PI tag1: 921~common~AMPS~AI
KINT | Kintore | 887 | 923 | PARK | FALSE | ('923~TR1~AMPS~AI')*1.732*0.011 | PI tag1: 923~TR1~AMPS~AI
KINT | Kintore | 887 | 941 | SKENE | FALSE | ('941~TR1~MW~AI'+'941~TR2~MW~AI') | PI tag1: 941~TR1~MW~AI; PI tag2: 941~TR2~MW~AI
KINT | Kintore | 887 | 962 | TORRYBURN | FALSE | ('962~T1~AMPS~AI'+'962~T2~AMPS~AI')*1.732*0.011 | 962~T1~AMPS~AI | 962~T2~AMPS~AI | 962A~C01~AMPS~AI | 962B~C01~AMPS~AI | 306~T1~AMPS~AI
LAIR | Lairg | 534 | 534 | LAIRG GRID | TRUE | Lower Ollach Primary substation 2018-19 | PI tag1: 623~11KV~AMPS~AI
LAIR | Lairg | 534 | 540 | TORBOLL | FALSE | No PI tag
LAIR | Lairg | 534 | 548 | TRESSADY | FALSE | No PI tag
LUNA | Lunanhead | 81 | 81 | LUNANHEAD GRID | TRUE
LUNA | Lunanhead | 81 | 89 | FRIOCKHEIM | FALSE | ('089~T1_T2_11~AMPS~AI')*1.732*0.011 | PI tag1: 089~T1_T2_11~AMPS~AI; PI tag2: 089A~CO1~AMPS~AI; PI tag3: 089B~C01~AMPS~AI
LUNA | Lunanhead | 81 | 87 | INVERARITY | FALSE | ('087~TR1~MW~AI')*1.732*0.011 | PI tag1: 087~TR1~MW~AI; PI tag2: 087~002~AMPS~AI; PI tag3: 087~003~AMPS~AI; PI tag4: 087~GT1_11~AMPS~AI
LUNA | Lunanhead | 81 | 83 | LOCHSIDE | FALSE | ('083~T1_T2_11~AMPS~AI')*1.732*0.011 | PI tag1: 083~T1_T2_11~AMPS~AI
LUNA | Lunanhead | 81 | 82 | LUNANHEAD | FALSE | ('082~T1_T2_11~AMPS~AI')*1.732*0.011 | 082~T1_T2_11~AMPS~AI | GEN473M_02 | 082A~C01~MW~AI | 082B~C01~MW~AI | 082C~C01~AMPS~AI | 082C~C01~KV~AI | 082D~C01~MW~AI
LUNA | Lunanhead | 81 | 84 | MARYTON | FALSE | ('084~T1_T2_11~AMPS~AI')*1.732*0.011 | PI tag1: 084~T1_T2_11~AMPS~AI
LYND | Lyndhurst | 11 | 11 | LYNDHURST GRID | TRUE
LYND | Lyndhurst | 11 | 13 | LOCHEE | FALSE | ('013~TR1~MW~AI'+'013~TR2~MW~AI') | PI tag1: 013~TR1~MW~AI; PI tag2: 013~TR2~MW~AI
LYND | Lyndhurst | 11 | 12 | LYNDHURST | FALSE | ('012~001~AMPS~AI'+'012~002~AMPS~AI'+'012~003~AMPS~AI'+'012~004~AMPS~AI'+'012~005~AMPS~AI'+'012~006~AMPS~AI'+'012~007~AMPS~AI')*1.732*0.011 | 012~001~AMPS~AI | 012~002~AMPS~AI | 012~003~AMPS~AI | 012~004~AMPS~AI | 012~005~AMPS~AI | 012~006~AMPS~AI | 012~007~AMPS~AI
LYND | Lyndhurst | 11 | 14 | MACALPINE ROAD | FALSE | ('014~TR1~MW~AI'+'014~TR2~MW~AI') | 014~TR1~MW~AI | 014~TR2~MW~AI | 014~001~AMPS~AI | 014~003~AMPS~AI | 014~005~AMPS~AI | 014~006~AMPS~AI
LYND | Lyndhurst | 11 | 15 | WEST KIRKTON | FALSE | ('015~T2_T3~AMPS~AI')*1.732*0.011 | PI tag1: 015~T2_T3~AMPS~AI
MACD | MacDuff | 405 | 405 | MACDUFF | TRUE | Markethill Primary substation 2018-19 (Disconnected) | PI tag1: 742~011~AMPS~AI
MILC | Milton of Craigie | 51 | 51 | MILTON OF CRAIGIE GRID | TRUE | Marnoch Primary substation 2018-19 | PI tag1: 401~T1_T2~AMPS~AI
MACD | Macduff | 405 | 406 | Macduff New | FALSE | ('406~TR1~AMPS~AI'+'406~TR2~AMPS~AI')*1.732*0.011 | 406~TR1~AMPS~AI | 406~TR2~AMPS~AI | 406A~C01~AMPS~AI | 406A~C01~KV~AI | 406A~C01~MVAR~AI | 406A~C01~MW~AI | 406B~C01~AMPS~AI
MILC | Milton of Craigie | 51 | 55 | ASHLUDIE | FALSE | ('055~T1_T2_11~AMPS~AI')*1.732*0.011 | PI tag1: 055~T1_T2_11~AMPS~AI; PI tag2: GEN469_2
MILC | Milton of Craigie | 51 | 56 | BALDOVIE | FALSE | ('056~T1_T2_11~AMPS~AI')*1.732*0.011 | PI tag1: 056~T1_T2_11~AMPS~AI
MILC | Milton of Craigie | 51 | 57 | BROUGHTY FERRY | FALSE | ('057~TR1~MW~AI'+'057~TR2~MW~AI') | PI tag1: 057~TR1~MW~AI; PI tag2: 057~TR2~MW~AI
MILC | Milton of Craigie | 51 | 58 | EDZELL STREET | FALSE | ('058~T1_T2~AMPS~AI')*1.732*0.011 | PI tag1: 058~T1_T2~AMPS~AI
MILC | Milton of Craigie | 51 | 54 | LONGHAUGH | FALSE | ('054~T1_T2_T3~AMPS~AI')*1.732*0.011 | PI tag1: 054~T1_T2_T3~AMPS~AI; PI tag2: 054A~C01~MW~AI; PI tag3: 054A~C01~AMPS~AI
MILC | Milton of Craigie | 51 | 52 | MILTON OF CRAIGIE | FALSE | ('057~TR1~MW~AI') | PI tag1: 052~TR1~MW~AI
MILC | Milton of Craigie | 51 | 53 | OLD CRAIGIE ROAD | FALSE | ('053~T2~AMPS~AI')*1.732*0.011 | PI tag1: 053~T2~AMPS~AI
MYBS | Mybster | 586 | 591 | BETTYHILL | FALSE | ('591~11KV~AMPS~AI')*1.732*0.011 | PI tag1: 591~11KV~AMPS~AI
MYBS | Mybster | 586 | 586 | MYBSTER GRID | TRUE | Midmar Primary substation 2018-19 | PI tag1: 907~T1~AMPS~AI
MYBS | Mybster | 586 | 581 | COLDBACKIE | FALSE | ('581~11KV~AMPS~AI')*1.732*0.011 | PI tag1: 581~11KV~AMPS~AI
MYBS | Mybster | 586 | 584 | LATHERON | FALSE | ('584~TR1~AMPS~AI')*1.732*0.011 | PI tag1: 584~TR1~AMPS~AI
MYBS | Mybster | 586 | 590 | MELVICH | FALSE | ('590~11KV~AMPS~AI')*1.732*0.011 | PI tag1: 590~11KV~AMPS~AI
MYBS | Mybster | 586 | 594 | WICK | FALSE | ('594~TR1~MW~AI'+'594~TR2~MW~AI') | PI tag1: 594~TR1~MW~AI; PI tag2: 594~TR2~MW~AI
NAIR | Nairn | 733 | 779 | ARDERSIER | FALSE | ('779~T1_T2~AMPS~AI')*1.732*0.011 | PI tag1: 779~T1_T2~AMPS~AI
NAIR | Nairn | 733 | 752 | DALCROSS | FALSE | ('752~11KV~AMPS~AI')*1.732*0.011 | PI tag1: 752~11KV~AMPS~AI
NAIR | Nairn | 733 | 733 | NAIRN GRID | TRUE | Mossat Primary substation 2018-19 | PI tag1: 911~common~AMPS~AI |  | Lethen Primary Substation 2018-19 | 703~T1~AMPS~AI
NAIR | Nairn | 733 | 452 | FORRES | FALSE | ('452~TR1~MW~AI'+'452~TR2~MW~AI') | PI tag1: 452~TR1~MW~AI; PI tag2: 452~TR2~MW~AI; PI tag3: 452~T1_T2_11~AMPS~AI
NAIR | Nairn | 733 | 703 | LETHEN | FALSE | ('703~T1~AMPS~AI')*1.732*0.011 | PI tag1: 703~T1~AMPS~AI
ORRI | Orrin | 565 | 565 | ORRIN | TRUE | Muir of Ord substation 2018-19 | PI tag1: 547~T1_T2~AMPS~AI
GLFA | Glenfarclas | 474 | 474 | GLENFARCLAS | TRUE | Muirend Primary substation 2018-19 | PI tag1: 542~TR1~AMPS~AI
PEHG | Peterhead Grange | 927 | 927 | PETERHEAD GRANGE 33kV | TRUE | Nairn Central Primary substation 2018-19 | PI tag1: 733~1L5~AMPS~AI
NAIR | Nairn | 733 | 723 | NAIRN CENTRAL | FALSE | ('733~1L5~AMPS~AI')*1.732*0.011 | PI tag1: 733~1L5~AMPS~AI
PERS | Persley | 925 | 814 | BRIDGE OF DON | FALSE | ('814~TR2~AMPS~AI'+'814~TR1~AMPS~AI')*1.732*0.011 | PI tag1: 814~TR2~AMPS~AI; PI tag2: 814~TR1~AMPS~AI
PEHS | Peterhead Shell | 926 | 926 | PETERHEAD SHELL | TRUE
PERS | Persley | 925 | 865 | HAUDAGAIN | FALSE | ('865~common~AMPS~AI')*1.732*0.011 | PI tag1: 865~common~AMPS~AI
PERS | Persley | 925 | 912 | MUGIEMOSS MILLS | FALSE | No PI tag
PERS | Persley | 925 | 917 | NORTHFIELD | FALSE | ('917~TR1~AMPS~AI')*1.732*0.011 | PI tag1: 917~TR1~AMPS~AI
PERS | Persley | 925 | 924 | PERSLEY SUPERGRID | FALSE | No PI tag
PERS | Persley | 925 | 956 | ST MACHAR | FALSE | ('956~TR1~AMPS~AI'+'956~TR2~AMPS~AI')*1.732*0.011 | PI tag1: 956~TR1~AMPS~AI; PI tag2: 956~TR2~AMPS~AI
PERS | Persley | 925 | 475 | STONEYHILL | FALSE | ('475~T1~MW~AI') | PI tag1: 475~T1~MW~AI
PERS | Persley | 925 | 476 | STONEYHILL BIOMASS | FALSE | No PI tag
PERS | Persley | 925 | 925 | PERSLEY GRID | TRUE | North Kessock Primary 2018-19 | PI tag1: 558~TR1~AMPS~AI
PERS | Persley | 925 | 947 | STONEYWOOD | FALSE | ('947~TR1~AMPS~AI'+'947~TR2~AMPS~AI')*1.732*0.011 | PI tag1: 947~TR1~AMPS~AI; PI tag2: 947~TR2~AMPS~AI
PERS | Persley | 925 | 982 | WHITESTRIPES | FALSE | ('982~common~AMPS~AI')*1.732*0.011 | PI tag1: 982~common~AMPS~AI
PEHG | Peterhead Grange | 927 | 928 | PETERHEAD GRANGE 11kV | FALSE | ('928~001~AMPS~AI')*1.732*0.011 | PI tag1: 928~001~AMPS~AI
PORA | Port Ann | 301 | 301 | PORT ANN GRID | TRUE | North Street Primary 2018-19 | PI tag1: 929~common~AMPS~AI
PEHG | Peterhead Grange | 927 | 929 | PHEAD NORTH ST | FALSE | ('929~common~AMPS~AI')*1.732*0.011 | PI tag1: 929~common~AMPS~AI
PORA | Port Ann | 301 | 319 | AIRIGH-NA-BRODAIG | FALSE | No PI tag
PORA | Port Ann | 301 | 313 | BOWMORE | FALSE | ('313~TR1~MW~AI') | PI tag1: 313~TR1~MW~AI
PORA | Port Ann | 301 | 305 | CRINAN | FALSE | ('305~COMMON~AMPS~AI')*1.732*0.011 | PI tag1: 305~COMMON~AMPS~AI
PORA | Port Ann | 301 | 332 | FURNACE QUARRY | FALSE | No PI tag
PORA | Port Ann | 301 | 309 | INVERNEIL | FALSE | ('309~T1~AMPS~AI')*1.732*0.011 | PI tag1: 309~T1~AMPS~AI
PORA | Port Ann | 301 | 308 | LOCHGILPHEAD | FALSE | ('308~T1~MW~AI'+'308~T1~MW~AI') | PI tag1: 308~T1~MW~AI; PI tag2: 308~T1~MW~AI
PORA | Port Ann | 301 | 339 | LUSSAGIVEN | FALSE | No PI tag
PORA | Port Ann | 301 | 334 | PORT ASKAIG | FALSE | ('334~common~AMPS~AI')*1.732*0.011 | PI tag1: 334~common~AMPS~AI
PORA | Port Ann | 301 | 331 | PORT ELLEN | FALSE | ('331~common~AMPS~AI')*1.732*0.011 | PI tag1: 331~common~AMPS~AI
PORA | Port Ann | 301 | 397 | STONEFIELD | FALSE | No PI tag
PORA | Port Ann | 301 | 341 | TARBERT JURA | FALSE | No PI tag
PORA | Port Ann | 301 | 310 | TARBERT LOCH FYNE | FALSE | ('310~TR1~MW~AI'+'310~TR2~MW~AI') | PI tag1: 310~TR1~MW~AI; PI tag2: 310~TR2~MW~AI; PI tag3: 310A~C01~AMPS~AI; PI tag4: 310A~C01~AMPS~AI
PORA | Port Ann | 301 | 391 | TAYVALLICH | FALSE | No demand connected, it’s a regulator
RANN | Rannoch | 261 | 343 | BLACKMOUNT | FALSE | No PI tag
RANN | Rannoch | 261 | 261 | RANNOCH GRID | TRUE | Pinegrove Primary 2018-19 | PI tag1: 734~T1_T2~AMPS~AI
RANN | Rannoch | 261 | 274 | BRIDGE OF GAUR | FALSE | No PI tag
RANN | Rannoch | 261 | 345 | GLENETIVE | FALSE | No PI tag
RANN | Rannoch | 261 | 218 | TYNDRUM | FALSE | ('218~TR1~MW~AI') | PI tag1: 218~TR1~MW~AI
REDM | Redmoss | 934 | 813 | BP NETHERLEY | FALSE | ('813~1C0_T1~AMPS~AI'+'813~2C0_GT2~AMPS~AI')*1.732*0.033 | PI tag1: 813~1C0_T1~AMPS~AI; PI tag2: 813~2C0_GT2~AMPS~AI
REDM | Redmoss | 934 | 882 | KINCORTH | FALSE | ('934~7L5~MW~AI') | PI tag1: 934~7L5~MW~AI
REDM | Redmoss | 934 | 915 | NEWTONHILL | FALSE | ('915~common~AMPS~AI')*1.732*0.011 | PI tag1: 915~common~AMPS~AI
REDM | Redmoss | 934 | 934 | REDMOSS GRID | TRUE | Portree Primary 2018-19 | PI tag1: 632~T1~AMPS~AI |  | Redmoss Primary 2018-19 | 935~TR1~AMPS~AI
REDM | Redmoss | 934 | 935 | REDMOSS | FALSE | ('935~TR1~AMPS~AI')*1.732*0.011 | PI tag1: 935~TR1~AMPS~AI
SFEG | St Fergus Gas | 955 | 955 | ST FERGUS GAS TERM | TRUE
SHIN | Shin | 545 | 523 | GLEDFIELD | FALSE | ('523~T1~AMPS~AI')*1.732*0.011 | PI tag1: 523~T1~AMPS~AI
SFIL | St Fillans | 213 | 213 | ST FILLANS P S | TRUE | Queens Lane North Primary 2018-19 | PI tag1: 932~TR1~Amps~AI |  | St Fillans 33kV Load 2018-19 | LEDP~G1~MW~AI
SHIN | Shin | 545 | 536 | SHIN | FALSE | ('545~T3~MW~AI') | PI tag1: 545~T3~MW~AI; PI tag2: 545A~1C0~MW~AI; PI tag3: 545B~1C0~MW~AI
SLOY | Sloy | 367 | 377 | ARROCHAR | FALSE | No PI tag
SHIN | Shin | 545 | 545 | SHIN GRID | TRUE | No PI tag
SLOY | Sloy | 367 | 139 | SLOY POWER STATION | FALSE | No PI tag
SLOY | Sloy | 367 | 367 | SLOY GRID | TRUE | Raigmore Primary 2018-19 | PI tag1: 735~014~AMPS~AI
SFIL | St Fillans | 213 | 212 | DALCHONZIE | FALSE | ('212~TR2~MW~AI') | PI tag1: 212~TR2~MW~AI
STHA | Strathleven | 202 | 202 | STRATHLEVEN | TRUE
STHA | Strathleven | 202 | 206 | ABERFOYLE | FALSE | ('206~T1~MW~AI') | PI tag1: 206~T1~MW~AI; PI tag2: 206C~CO1~AMPS~AI
STHA | Strathleven | 202 | 285 | AUCHENCARROCH | FALSE | No PI tag
STHA | Strathleven | 202 | 220 | BLAIRLINNANS | FALSE | ('220~011~AMPS~AI')*1.732*0.011 | PI tag1: 220~011~AMPS~AI
STHA | Strathleven | 202 | 203 | DRYMEN | FALSE | ('203~T1~AMPS~AI')*1.732*0.011 | PI tag1: 203~T1~AMPS~AI; PI tag2: 203~BUSBAR~KV~AI; PI tag3: 203A~C01~MW~AI
STHA | Strathleven | 202 | 205 | KEPCULLOCH | FALSE | ('205~SUMM~AMPS~AI')*1.732*0.011 | PI tag1: 205~SUMM~AMPS~AI
STHA | Strathleven | 202 | 204 | KILLEARN | FALSE | ('204~T1~MW~AI') | PI tag1: 204~T1~MW~AI
STHA | Strathleven | 202 | 239 | ROSS PRIORY PUMPING STAT. | FALSE | ('239~1C0~MW~AI'+'239~2C0~MW~AI') | PI tag1: 239~1C0~MW~AI; PI tag2: 239~2C0~MW~AI
STRI | Strichen | 949 | 812 | BODDAM | FALSE | ('812~006~AMPS~AI')*1.732*0.011 | PI tag1: 812~006~AMPS~AI; PI tag2: 812~TR1~KV~AI
STRI | Strichen | 949 | 863 | HATTON | FALSE | ('863~T1~MW~AI'+'863~T2~MW~AI') | 863~T1~MW~AI | 863~T2~MW~AI | Replaced with | 863~common~KV~AI | Can also be used the PI Tags for the 11kV feeder (5)
STRI | Strichen | 949 | 901 | MAUD | FALSE | ('901~common~AMPS~AI')*1.732*0.011 | PI tag1: 901~common~AMPS~AI; PI tag2: 901A~C01~AMPS~AI; PI tag3: 901A~C01~MW~AI
STRI | Strichen | 949 | 909 | MINTLAW | FALSE | ('909~T1~MW~AI'+'909~T2~MW~AI') | 909~T1~MW~AI | 909~T2~MW~AI | 0 | 909B~CO1~MW~AI | 909A~C01~MW~AI
STRI | Strichen | 949 | 913 | NEW PITSLIGO | FALSE | ('913~common~AMPS~AI')*1.732*0.011 | PI tag1: 913~common~AMPS~AI
STRI | Strichen | 949 | 949 | STRICHEN GRID | TRUE | Ruthrieston Primary substation 2018-19 | PI tag1: CRAI~QLN2~AMPS~AI
STRI | Strichen | 949 | 950 | STRICHEN | FALSE | ('949~T1~MW~AI'+'949~T2~MW~AI') | 949~T1~MW~AI | 949~T2~MW~AI | 950A~C01~AMPS~AI | 950A~C01~KV~AI | 950B~C01~MW~AI | 950C~C01~MW~AI | 950D~C01~MW~AI | 950E~C01~MW~AI | 950F~C01~MW~AI
TARL | Tarland | 470 | 470 | TARLAND GRID | TRUE
TARL | Tarland | 470 | 801 | ABOYNE | FALSE | ('801~T1~MW~AI'+'801~T2~MW~AI') | PI tag1: 801~T1~MW~AI; PI tag2: 801~T2~MW~AI
TARL | Tarland | 470 | 806 | BALLATER | FALSE | ('806~common~AMPS~AI')*1.732*0.011 | 806~common~AMPS~AI | 806~001~AMPS~AI | 806~002~AMPS~AI | 806~004~AMPS~AI | 806~005~AMPS~AI | 806~006~AMPS~AI | 806~common~AMPS~AI
TARL | Tarland | 470 | 911 | MOSSAT | FALSE | ('911~common~AMPS~AI')*1.732*0.011 | PI tag1: 911~common~AMPS~AI
TARL | Tarland | 470 | 951 | STRATHDON | FALSE | ('951~TR1~AMPS~AI')*1.732*0.011 | PI tag1: 951~TR1~AMPS~AI; PI tag8: 950E~C01~MW~AI
TARL | Tarland | 470 | 981 | WHITEHOUSE | FALSE | ('981~T1_T2~AMPS~AI')*1.732*0.011 | PI tag1: 981~T1_T2~AMPS~AI
TAYN | Taynuilt | 303 | 303 | TAYNUILT GRID | TRUE | Sandbank Primary substation 2018-19 | PI tag1: 364~002~AMPS~AI; PI tag2: 364~003~AMPS~AI; PI tag3: 364~004~AMPS~AI; PI tag4: 364~005~AMPS~AI
TAYN | Taynuilt | 303 | 344 | ARDTUN REGULATOR | FALSE | Just a regulator
TAYN | Taynuilt | 303 | 327 | BARCALDINE | FALSE | ('327~TR1~AMPS~AI')*1.732*0.011 | PI tag1: 327~TR1~AMPS~AI
TAYN | Taynuilt | 303 | 394 | BEOCHLICH | FALSE | No PI tag
TAYN | Taynuilt | 303 | 351 | BLARGHOUR | FALSE | Not found
TAYN | Taynuilt | 303 | 328 | BONAWE | FALSE | No PI tag
TAYN | Taynuilt | 303 | 306 | CONNEL | FALSE | ('306~T1~AMPS~AI')*1.732*0.011 | PI tag1: 306~T1~AMPS~AI; PI tag2: 306~common~KV~AI
TAYN | Taynuilt | 303 | 381 | CRAIGAGOUL | FALSE | NO demand directly connected. This sub feeds to Rothesay
TAYN | Taynuilt | 303 | 348 | DALMALLY | FALSE | No PI tag
TAYN | Taynuilt | 303 | 346 | DERVAIG | FALSE | ('346~SS~AMPS~AI')*1.732*0.011 | PI tag1: 346~SS~AMPS~AI; PI tag2: 346~SS~KV~AI; PI tag3: 314A~C01~AMPS~AI; PI tag4: 314A~C01~AMPS~AI
TAYN | Taynuilt | 303 | 324 | EREDINE | FALSE | No PI tag
TAYN | Taynuilt | 303 | 329 | KENMORE | FALSE | No PI tag
TAYN | Taynuilt | 303 | 335 | KERRERA | FALSE | No PI tag
TAYN | Taynuilt | 303 | 323 | KILCHRENAN | FALSE | ('323~SS~AMPS~AI')*1.732*0.011 | PI tag1: 323~SS~AMPS~AI; PI tag2: 323~common~KV~AI; PI tag3: 323~SS~AMPS~AI; PI tag4: B323R~common~AMPS~AI
TAYN | Taynuilt | 303 | 304 | KILMELFORD PS | FALSE | ('304~1T0~AMPS~AI')*1.732*0.011 | PI tag1: 304~1T0~AMPS~AI; PI tag2: KILM~G1~MW~AI; PI tag3: 304~2L5~AMPS~AI
TAYN | Taynuilt | 303 | 322 | KILNINVER | FALSE | ('322~11KV_SS~AMPS~AI')*1.732*0.011 | PI tag1: 322~11KV_SS~AMPS~AI; PI tag2: 322A~C01~AMPS~AI
TAYN | Taynuilt | 303 | 333 | KINLOCH | FALSE | ('333~T1~MW~AI')*1.732*0.011 | 333~T1~MW~AI | 333~PEAK~PERCENT~AI | 333~T1~AMPS~AI | 333~T1~KV~AI | 333~T1~MVAR~AI | 333~T1~MW~AI
TAYN | Taynuilt | 303 | 317 | LOCHDONHEAD | FALSE | ('317~T1~MW~AI') | PI tag1: 317~T1~MW~AI
TAYN | Taynuilt | 303 | 307 | OBAN | FALSE | ('307~TR1~AMPS~AI')*1.732*0.011 | PI tag1: 307~TR1~AMPS~AI
TAYN | Taynuilt | 303 | 315 | SALEN, Mull Primary | FALSE | ('315~TR1~AMPS~AI')*1.732*0.011 | PI tag1: 315~TR1~AMPS~AI
TAYN | Taynuilt | 303 | 340 | SCAMMADALE | FALSE | No PI tag
TAYN | Taynuilt | 303 | 316 | STRAND REGULATOR | FALSE | it’s a regulator only
TAYN | Taynuilt | 303 | 347 | TAYNUILT | FALSE | ('347~TAYNUILT~AMPS~AI')*1.732*0.011 | PI tag1: 347~TAYNUILT~AMPS~AI
TAYN | Taynuilt | 303 | 314 | TIREE | FALSE | although there is a PI tag (314~SITE~AMPS~AI) No transformer identified at this site
TAYN | Taynuilt | 303 | 342 | TIRORAN BRIDGE | FALSE | No PI tag
THSO | Thurso | 592 | 701 | BURGARHILL | FALSE | ('701~011_012~AMPS~AI')*1.732*0.011 | 701~011_012~AMPS~AI | 701A~1C0~AMPS~AI | 701A~1C0~KV~AI | 701A~1C0~MVAR~AI | 701A~1C0~MW~AI | 701A~2K0~KV~AI
THSO | Thurso | 592 | 675 | EDAY | FALSE | ('675~11KV~AMPS~AI')*1.732*0.011 | PI tag1: 675~11KV~AMPS~AI
THSO | Thurso | 592 | 492 | EDAY TIDAL STREAM | FALSE | ('492~TR1~MW~AI') | PI tag1: 492~TR1~MW~AI
THSO | Thurso | 592 | 680 | FLOTTA | FALSE | ('680~TR1~AMPS~AI')*1.732*0.011 | 680~TR1~AMPS~AI | 680~common~KV~AI | 680A~1C0~MW~AI | 680B~C01~MW~AI | 680~TR1~AMPS~AI
THSO | Thurso | 592 | 583 | FORSS | FALSE | ('583~TR1~AMPS~AI')*1.732*0.011 | PI tag1: 583~TR1~AMPS~AI; PI tag2: FORSWF~common~MW~AI
THSO | Thurso | 592 | 597 | HALKIRK | FALSE | ('597~TR1~MW~AI') | PI tag1: 597~TR1~MW~AI
THSO | Thurso | 592 | 582 | HASTIGROW | FALSE | ('582~TR1~AMPS~AI')*1.732*0.011 | PI tag1: 582~TR1~AMPS~AI
THSO | Thurso | 592 | 677 | KIRKWALL | FALSE | ('677~T1~MW~AI'+'677~T2~MW~AI') | 677~T1~MW~AI | 677~T2~MW~AI | 677A~C01~MW~AI | 677A~C01~_~AI | 677A~C01~AMPS~AI | 677A~C01~KV~AI | 677A~C01~MVAR~AI
THSO | Thurso | 592 | 592 | THURSO GRID | TRUE | Tarbert Loch Fyne Primary substation 2018-19 | 310~TR1~MW~AI | 310~TR2~MW~AI | 310A~C01~AMPS~AI | 310A~C01~AMPS~AI | 310A~C01~KV~AI | 310~TR1~MW~AI | 310~TR2~MW~AI |  |  | Ormlie Primary 2018-19 | 587~T1~AMPS~AI
THSO | Thurso | 592 | 571 | LAREL | FALSE | No PI tag
THSO | Thurso | 592 | 682 | LYNESS | FALSE | ('682~011~AMPS~AI')*1.732*0.011 | PI tag1: 682~011~AMPS~AI
THSO | Thurso | 592 | 585 | MOUNT PLEASANT | FALSE | ('585~T1~AMPS~AI')*1.732*0.011 | PI tag1: 585~T1~AMPS~AI
THSO | Thurso | 592 | 681 | NORTH HOY | FALSE | No PI tag
THSO | Thurso | 592 | 587 | ORMLIE | FALSE | ('587~T1~AMPS~AI')*1.732*0.011 | PI tag1: 587~T1~AMPS~AI
THSO | Thurso | 592 | 489 | RACKWICK PRIMARY | FALSE | No PI tag
THSO | Thurso | 592 | 498 | ROUSAY | FALSE | ('498~011~MW~AI') | PI tag1: 498~011~MW~AI
THSO | Thurso | 592 | 685 | SANDAY | FALSE | ('685~011~AMPS~AI')*1.732*0.011 | PI tag1: 685~011~AMPS~AI
THSO | Thurso | 592 | 673 | SCORRADALE | FALSE | this is not a primary sub but more of a regulator at 33kV
THSO | Thurso | 592 | 683 | SHAPINSAY | FALSE | ('683~011~AMPS~AI')*1.732*0.011 | PI tag1: 683~011~AMPS~AI; PI tag2: 683~11~AMPS~AI
THSO | Thurso | 592 | 679 | ST MARYS | FALSE | ('679~TR1~AMPS~AI')*1.732*0.011 | 679~TR1~AMPS~AI | 679B~C01~KV~AI | 679B~C01~MVAR~AI | 679B~C01~MW~AI | 679B~C01~VOLTS~AI | 679B~DSTAT_SPC~KV~AI | 679B~DSTAT_SPC~VOLTS~AI
THSO | Thurso | 592 | 678 | STROMNESS | FALSE | ('678~TR1~MW~AI'+'678~TR2~MW~AI') | PI tag1: 678~TR1~MW~AI; PI tag2: 678~TR2~MW~AI; PI tag3: 678A~C01~MW~AI; PI tag4: 678~096~MW~AI
THSO | Thurso | 592 | 684 | STRONSAY | FALSE | ('684~011~AMPS~AI')*1.732*0.011 | PI tag1: 684~011~AMPS~AI
THSO | Thurso | 592 | 674 | WESTRAY | FALSE | ('674~001~AMPS~AI')*1.732*0.011 | PI tag1: 674~001~AMPS~AI
TUMB | Tummel Bridge | 260 | 260 | TUMMEL BRIDGE GRID | TRUE | Ullapool Primary substation 2018-19 | PI tag1: 549~071~AMPS~AI; PI tag2: 549~072~AMPS~AI
TUMB | Tummel Bridge | 260 | 267 | ABERFELDY | FALSE | ('267~T1~AMPS~AI'+'267~T2~AMPS~AI')*1.732*0.011 | PI tag1: 267~T1~AMPS~AI; PI tag2: 267~T2~AMPS~AI; PI tag3: 267A~C01~AMPS~AI
TUMB | Tummel Bridge | 260 | 266 | BONSKEID | FALSE | ('266~common~AMPS~AI')*1.732*0.011 | PI tag1: 266~common~AMPS~AI; PI tag2: 266~BBAR~KV~AI
TUMB | Tummel Bridge | 260 | 265 | CALVINE | FALSE | ('265~common~AMPS~AI')*1.732*0.011 | PI tag1: 265~common~AMPS~AI
TUMB | Tummel Bridge | 260 | 268 | COSHIEVILLE | FALSE | ('268~001~AMPS~AI'+'268~002~AMPS~AI')*1.732*0.011 | PI tag1: 268~001~AMPS~AI; PI tag2: 268~002~AMPS~AI; PI tag3: 268~T1~KV~AI; PI tag4: GEN400_2
TUMB | Tummel Bridge | 260 | 276 | FINCASTLE | FALSE | there is no PI available for this primary
TUMB | Tummel Bridge | 260 | 262 | KINLOCH RANNOCH | FALSE | ('262~011~AMPS~AI')*1.732*0.011 | PI tag1: 262~011~AMPS~AI
TUMB | Tummel Bridge | 260 | 263 | PITLOCHRY | FALSE | ('263~TR1~AMPS~AI')*1.732*0.011 | PI tag1: 263~TR1~AMPS~AI
WIOW | Willowdale | 983 | 841 | DENBURN | FALSE | ('841~T1~Amps~ai'+'841~T2~Amps~ai')*1.732*0.011 | PI tag1: 841~T1~Amps~ai; PI tag2: 841~T2~Amps~ai; PI tag3: WIOW~8L5_FEED~AMPS~AI; PI tag4: 841~common~volts~ai
WIOW | Willowdale | 983 | 861 | GREYFRIARS | FALSE | ('861~TR1~AMPS~AI'+'861~TR2~AMPS~AI')*1.732*0.011 | PI tag1: 861~TR1~AMPS~AI; PI tag2: 861~TR2~AMPS~AI; PI tag3: 861A~C01~AMPS~AI
WIOW | Willowdale | 983 | 867 | HAYTON | FALSE | ('867~T1~MW~AI'+'867~T2~MW~AI') | 867~T1~MW~AI | 867~T2~MW~AI | 867~005~AMPS~AI | 867~010~AMPS~AI | 867~011~AMPS~AI | 867~012~AMPS~AI | 867~BBAR~KV~AI | 867~T1~AMPS~AI
WIOW | Willowdale | 983 | 958 | ST NICHOLAS | FALSE | ('958~TR1~AMPSB~AI')*1.732*0.011 | PI tag1: 958~TR1~AMPSB~AI
WIOW | Willowdale | 983 | 983 | WILLOWDALE | TRUE | [10 empty] | St Nicholas Primary substation 2018-19 | 958~TR1~AMPSB~AI
WOHI | Woodhill | 986 | 932 | QUEENS LANE NORTH | FALSE | ('932~TR1~Amps~AI')*1.732*0.011 | PI tag1: 932~TR1~Amps~AI
WOHI | Woodhill | 986 | 943 | SPRINGHILL | FALSE | ('WOHI~1L5~AMPS~AI'+'YWOHI~2L5~AMPS~AI'+'WOHI~5L5~AMPS~AI'+'WOHI~7L5~AMPS~AI')*1.732*0.011 | PI tag1: WOHI~1L5~AMPS~AI; PI tag2: YWOHI~2L5~AMPS~AI; PI tag3: WOHI~5L5~AMPS~AI; PI tag4: WOHI~7L5~AMPS~AI
WOHI | Woodhill | 986 | 985 | WOODHILL GRID | FALSE | ('986~TR3~AMPS~AI'+'986~T3~AMPS~AI')*1.732*0.011 | 986~TR3~AMPS~AI | 986~T3~AMPS~AI | 986~TR1~KV~AI | 986~TR3~KV~AI | 986C~C02~MW~AI | 986~T1~AMPS~AI | 986B~C01~MW~AI
WOHI | Woodhill | 986 | 986 | WOODHILL | TRUE
Note on G46: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: No PI tag available for this primary

## Sheet1
| NRN | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | NRN
Aberfeldy Primary substation 2018-19 (11KV DG) |  | 0: Tags; 1: 267~T1~AMPS~AI; 2: 267~T2~AMPS~AI; 3: Settlements Data; 4: 267A~C01~AMPS~AI | Tag | 267 | 267 | Set | 267 | 267 | 267 | 267 | 0
Aberfoyle Primary substation 2018-19 |  | 0: 206~T1~MW~AI; 1: 206C~CO1~AMPS~AI; 2: 206C~C01~KV~AI
Aberlour Primary substation 2018-19 |  | 0: 460~T1_T2~AMPS~AI
Abernethy Primary substation 2018-19 |  | 0: 241~T1~AMPS~AI
Aboyne Primary substation 2018-19 |  | 0: 801~T1~MW~AI; 1: 801~T2~MW~AI
Achiltibuie Primary substation 2018-19 |  | 0: 505~T1_11~AMPS~AI; 1: 505B~C01~MW~AI; 2: 505C~C01~AMPS~AI; 3: 505B~C01~AMPS~AI
Aird Primary substation 2018-19 (11kV DG) |  | 0: 671A~C01~AMPS~AI; 1: 671A~C01~AMPS~AI; 2: 671A~C01~KV~AI; 3: 671A~C01~MVAR~AI
Alyth Primary substation 2018-19 |  | 0: 258~011~AMPS~AI
Annat Primary substation 2018-19 (MW Tag) |  | 0: 702~TR1~MW~AI
Arderseir Primary substation 2018-19.xls |  | 0: 779~T1_T2~AMPS~AI
Arisaig Primary substation 2018-19 |  | 0: 740~T1~AMPS~AI
Ashgrove Primary substation 2018-19 |  | 0: 458~T1_T2~AMPS~AI
Ashludie Primary substation 2018-19 (11kV DG) |  | 0: 055~T1_T2_11~AMPS~AI; 1: GEN469_2
Aultbea substation 2018-19 (MW Tag) |  | 0: 504~T1~MW~AI
Aviemore Primary substation 2018-19 (New Tag) |  | 704~TR1~MW~AI | 704~TR2~MW~AI | 704~013~AMPS~AI | 704~014~AMPS~AI | 704~015~AMPS~AI | 704~016~AMPS~AI | 704~017~AMPS~AI
BP Balbeggie 33kV Customer 2018-19 |  | 0: 243~5L5~AMPS~AI
Balaldie Primary substation 2018-19 |  | 0: 552~097~AMPS~AI; 1: 552~098~AMPS~AI; 2: 552~099~AMPS~AI
Balbeggie Primary substation 2018-19 (MW Tag) |  | 0: 255~T1~MW~AI
Baldovie Primary substation 2018-19 |  | 0: 056~T1_T2_11~AMPS~AI; 1: 056~BBAR~KV~AI
Ballater Primary substation 2018-19 |  | 806~common~AMPS~AI | 806~001~AMPS~AI | 806~002~AMPS~AI | 806~004~AMPS~AI | 806~005~AMPS~AI | 806~006~AMPS~AI | 806~common~AMPS~AI
Balliekine Primary Substation 2018-19 |  | 0: 372~SS_LOAD~AMPS~AI
Ballindalloch Primary substation 2018-19 (MW Tags) |  | 0: 706~TR1~MW~AI; 1: 706~TR2~MW~AI
Ballure Primary substation 2018-19 |  | 318~common~AMPS~AI | 318A~C01~AMPS~AI | 318A~C01~KV~AI | 318A~C01~MVAR~AI | 318A~C01~MW~AI | 318~common~AMPS~AI
Balmedie Primary substation 2018-19 |  | 0: 807~common~AMPS~AI; 1: 807~NO1~KV~AI
Balnagask Primary substation 2018-19 |  | 0: CLAY~6L5~AMPS~AI
Banchory Primary substation 2018-19 |  | 0: 810~T1~MW~AI; 1: 810~T2~MW~AI
Barcaldine Primary substation 2018-19 |  | 0: 327~TR1~AMPS~AI
Barvas Primary substation 2018-19 |  | 0: 651~T1_T2~AMPS~AI; 1: 651~T1_T2~AMPS~AI; 2: 651~T1~AMPS~AI; 3: 651~T2~AMPS~AI
Battery Point Primary substation 2018-19 (MW Tags) - 3rd Tx Added |  | 0: 652~T1~MW~AI; 1: 652~T2~MW~AI; 2: 652~T3~MW~AI
Bettyhill Primary substation 2018-19 |  | 0: 591~11KV~AMPS~AI
Bilbohal Primary substation 2018-19 |  | 0: 499~T1_T2~AMPS~AI
Blackstand Primary substation 2018-19 |  | 0: 509~TR1~AMPS~AI; 1: 509~T1~KV~AI
Blairgowrie Primary substation 2018-19 |  | 0: 257~SUMM~AMPS~AI; 1: 257~BBAR~KV~AI
Blairlinnans Primary substation 2018-19 |  | 0: 220~011~AMPS~AI; 1: 220~011~AMPS~AI; 2: 220~011~VOLTS~AI
Boat of Garten Primary substation 2018-19 |  | 0: 707~T1~MW~AI; 1: 707~T2~MW~AI
Boddam Primary substation PI_Tag_812_006_2018-19 USE ME |  | 0: 812~006~AMPS~AI; 1: 812~TR1~KV~AI
Bonskeid Primary substation 2018-19 |  | 0: 266~common~AMPS~AI; 1: 266~BBAR~KV~AI
Bowmore Primary substation 2018-19 (MW Tags) |  | 0: 313~TR1~MW~AI
Brae Primary substation 2018-19
Brechin Primary substation 2018-19 |  | 0: 073~TR1~MW~AI; 1: 073~TR2~MW~AI
Bridge of Don Primary substation 2018-19 (11kV DG) |  | 0: 814~TR2~AMPS~AI; 1: 814~TR1~AMPS~AI; 2: 814~BBAR~KV~AI; 3: GEN488M_2; 4: SETTLEMENTS?
Bridge of Dun Primary substation 2018-19 |  | 0: 072~T1_11~AMPS~AI
Bridge of Earn Primary substation 2018-19 |  | 0: 279~003~AMPS~AI; 1: 279~004~AMPS~AI
Broadford Primary substation 2018-19 (MW Tags) |  | 0: 627~T1~MW~AI
Brodick Primary substation 2018-19 |  | 0: 370~T1~MW~AI; 1: 370~T2~MW~AI
Brora Primary substation 2018-19 MW |  | 0: 550~T1_T2~MW~AI
Broughty Ferry Primary substation 2018-19 MW |  | 0: 057~TR1~MW~AI; 1: 057~TR2~MW~AI
Bruchag Primary substation 2018-19 |  | 0: 365~TR1~MW~AI; 1: 365~TR2~MW~AI
Buckie Primary substation 2018-19 (11kV DG) |  | 0: 462~T1_T2~AMPS~AI; 1: 462A~CO1~MW~AI
Bunoich Primary substation 2018-19 |  | 0: 745~011~AMPS~AI
Burgar Hill Primary substation 2018-19 (11kV DG) |  | 701~011_012~AMPS~AI | 701A~1C0~AMPS~AI | 701A~1C0~KV~AI | 701A~1C0~MVAR~AI | 701A~1C0~MW~AI | 701A~1C0~Power_Factor~AI | 701A~2K0~KV~AI | 701A~2K0~MVAR~AI
Burghead Primary substation 2018-19 |  | 0: 454~T1_T2~AMPS~AI
Burghmuir Primary substation 2018-19 |  | 0: 246~T1_T2_11~AMPS~AI
Callander Primary substation 2018-19 |  | 210~002~AMPS~AI | 210~003~AMPS~AI | 210~004~AMPS~AI | 210~005~AMPS~AI | 210~006~AMPS~AI | 210~007~AMPS~AI
Callanish Primary substation 2018-19 |  | 670~011~AMPS~AI | 670A~C01~AMPS~AI | 670A~C01~KV~AI | 670A~C01~MVAR~AI | 670A~C01~MW~AI | 670A~DSTAT_SPC~KV~AI | 670A~DSTAT_SYS~MVAR~AI | 670A~DSTAT_SYS~MW~AI
Calvine Primary substation 2018-19 |  | 0: 265~common~AMPS~AI
Campbeltown Primary substation 2018-19 (11kV DG) MW tags |  | 312~TRANS~AMPS~AI | 312~BBAR~KV~AI | LUSSA~G2~MW~AI | LUSSA~G1~MW~AI | 312~TR1~MW~AI | 312~TR2~MW~AI
Caputh Primary substation 2018-19 |  | 0: 256~T1~MW~AI; 1: 256~T2~MW~AI
Carnoustie Primary substation 2018-19 |  | 0: 064~TR1~MW~AI; 1: 064~TR2~MW~AI
Chaorach Primary substation 2018-19 |  | 0: 140~001~AMPS~AI
Charles Avenue Primary substation 2018-19 |  | 0: 062~T1_T2_11~AMPS~AI
Charleston Primary substation 2018-19
Clachan Primary substation 2018-19 |  | 0: 653~TR2~AMPS~AI; 1: 653~T2~KV~AI
Clayhills Primary substation 2018-19 |  | 0: CLAY~4L5~AMPS~AI; 1: CLAY~5L5~AMPS~AI
Coldbackie Primary substation 2018-19 |  | 0: 581~11KV~AMPS~AI
Coll Primary substation 2018-19 |  | 672~TR1~AMPS~AI | 672A~C01~AMPS~AI | 672A~C01~KV~AI | 672A~C01~MVAR~AI | 672A~C01~MW~AI | 672~011~AMPS~AI | 672~012~AMPS~AI | 672~TR1~AMPS~AI
Commerce Street Primary substation 2018-19 |  | 0: 827~TR1~MW~AI; 1: 827~TR2~MW~AI
Connel Primary substation 2018-19 |  | 0: 306~T1~AMPS~AI; 1: 306~common~KV~AI; 2: 306~T1~AMPS~AI
Conon Bridge Primary substation 2018-19 |  | 0: 513~TR1~MW~AI; 1: 513~TR2~MW~AI
Constable Street Primary substation 2018-19 |  | 032~TR1~MW~AI | 032~TR2~MW~AI | 032~001~AMPS~AI | 032~002~AMPS~AI | 032~003~AMPS~AI | 032~004~AMPS~AI | 032~005~AMPS~AI | 032~006~AMPS~AI
Corran Primary substation 2018-19 |  | 0: 744~11KV~AMPS~AI; 1: Settlements Data; 2: 744~11KV~AMPS~AI; 3: 744~T1~_~AI; 4: 744~T1~KV~AI
Coshieville Primary substation 2018-19 (11kV DG) |  | 0: 268~001~AMPS~AI; 1: 268~002~AMPS~AI; 2: 268~T1~KV~AI; 3: GEN400_2; 4: Settlements
Coupar Angus Primary substation 2018-19 |  | 0: 243~1H0~AMPS~AI; 1: 243~2H0~AMPS~AI; 2: 243~1H0~MW~AI; 3: 243~2H0~MW~AI
Craigiebuckler Primary substation 2018-19
Craiginches Primary substation 2018-19 |  | 0: 832~TR1~MW~AI; 1: 832~TR2~MW~AI
Craigton Primary substation 2018-19 |  | 0: CRAI~CBL1~AMPS~AI
Crieff Primary substation 2018-19 (11kV DG) |  | 0: 2; 1: 0.15
Crinan Primary substation 2018-19 |  | 0: 305~COMMON~AMPS~AI
Cromalt Primary substation 2018-19 (MW Tags) |  | 0: 326~TR1~MW~AI
Crosshills Primary substation 2018-19 |  | 0: 551~T1_T2~AMPS~AI
Cullen Primary substation 2018-19 |  | 0: 469~TR1~MW~AI
Culloden Primary substation 2018-19 |  | 0: 712~T1~AMPS~AI; 1: 712~T2~AMPS~AI
Culter Primary substation 2018-19 |  | 0: 836~TR1~MW~AI; 1: 836~TR2~MW~AI
Cumming Street Primary substation 2018-19 |  | 0: 457~T1_T2~AMPS~AI
Dalchonzie Primary substation 2018-19 |  | 0: 212~TR2~MW~AI
Dalcross Primary substation 2018-19 |  | 0: 752~11KV~AMPS~AI
Dalneigh Primary substation 2018-19 |  | 0: 713~T1_T2~AMPS~AI
Dalrulzion Primary substation 2018-19 |  | 0: 259~T1~AMPS~AI; 1: 259~T2~AMPS~AI; 2: 259~T2~KV~AI
Dalwhinnie Primary substation 2018-19 |  | 0: 777~011~AMPS~AI; 1: 777~11KV~_~AI; 2: 777~11KV~CURRENT~AI
Denburn Primary substation 2018-19 - |  | 0: WIOW~8L5_FEED~AMPS~AI; 1: 841~T1~Amps~ai; 2: 841~T2~Amps~ai; 3: 841~common~volts~ai
Dervaig (incl Tiree) Primary substation 2018-19 |  | 0: 346~SS~AMPS~AI; 1: 346~SS~KV~AI; 2: 314A~C01~AMPS~AI; 3: 314A~C01~AMPS~AI
Dingwall Primary substation 2018-19 (11kV DG) |  | 0: Little Wyvis; 1: Falls of Conis
Dornoch Primary substation 2018-19 |  | 0: 557~T1~AMPS~AI; 1: 557~T1~KV~AI
Douglas Pier Primary substation 2018-19 (11kV DG) |  | 0: 388~TRANS~AMPS~AI; 1: GEN406_2
Dounreay Primary substation 2018-19 |  | 598~T1~MW~AI | 598~T2~MW~AI | 598~1S0~AMPS~AI | 598~1S0~KV~AI | 598~1S0~MVAR~AI | 598~1S0~MW~AI | 598~6L5~AMPS~AI | 598~6L5~KV~AI | 598~6L5~MVAR~AI
Drimore Primary substation 2018-19 |  | 0: 644~T1~AMPS~AI; 1: 644~T1~KV~AI
Drumadrochit Primary substation 2018-19_completed |  | 0: 517~TR1~AMPS~AI; 1: 517A~C01~AMPS~AI
Drymen Primary substation 2018-19_completed |  | 0: 203~T1~AMPS~AI; 1: 203~BUSBAR~KV~AI; 2: 203A~C01~MW~AI
Drynoch Primary substation 2018-19_completed |  | 0: 629~T1~AMPS~AI; 1: 629~011~AMPS~AI; 2: 629~012~AMPS~AI; 3: 629~T1~AMPS~AI
Dufftown substation 2018-19_completed |  | 0: 461~T1_T2~AMPS~AI; 1: 461~T1_T2~AMPS~AI
Dunblane Primary substation 2018-19_completed |  | 0: 209~SUMM~AMPS~AI; 1: 209~BBAR~KV~AI
Dunoon Primary substation 2018-19_completed |  | 0: 363~SUMM~AMPS~AI; 1: 363~BBAR~KV~AI
Dunvegan Primary substation 2018-19_completed |  | 0: 638~T1~AMPS~AI
Dyce North Primary substation 2018-19 MW_completed
Eday Primary substation 2018-19_completed |  | 0: 675~11KV~AMPS~AI
Edzell Primary substation 2018-19_completed |  | 0: 847~common~AMPS~AI; 1: 847A_C01_AMPSn
Edzell Street Primary substation 2018-19_completed |  | 0: 058~T1_T2~AMPS~AI
Elgin Primary substation 2018-19_completed |  | 0: 482~T1_T2~AMPS~AI; 1: 482~11_BBAR~KV~AI
Elliot Depot Primary substation 2018-19_completed |  | 0: 068~T1_11~AMPS~AI
Ellon Primary substation 2018-19_completed |  | 0: 849~common~AMPS~AI; 1: 849A~TR1~AMPS~AI; 2: 849A~TR2~AMPS~AI
Errol Primary substation 2018-19_completed |  | 0: 254~SUMM~AMPS~AI; 1: 254~SS~KV~AI; 2: 254A~C01~AMPS~AI
Fasnakyle Primary substation 2018-19_completed |  | 0: FASN~T5~AMPS~AI
Firth Primary substation 2018-19_completed |  | 0: 692~T2_11KV~AMPS~AI; 1: 692~11KV~KV~AI
Flotta Primary substation 2018-19_completed |  | 0: 680~TR1~AMPS~AI; 1: 680~common~KV~AI; 2: 680A~1C0~MW~AI; 3: 680B~C01~MW~AI; 4: 680~TR1~AMPS~AI
Fochabers Primary substation 2018-19_completed |  | 0: 487~11KV~AMPS~AI
Forres Primary substation 2018-19_completed |  | 0: 452~T1_T2_11~AMPS~AI; 1: 452~TR1~MW~AI; 2: 452~TR2~MW~AI
Forss Primary substation 2018-19 (11kV DG)_completed |  | 0: 583~TR1~AMPS~AI; 1: FORSWF~common~MW~AI
Forteviot Primary substation 2018-19_completed |  | 253~TR1~MW~AI | 253~001~AMPS~AI | 253~T1~TAP_POSITION~AI | 253~TR1~AMPS~AI | 253~TR1~KV~AI | 253~TR1~MVAR~AI | 253~TR1~MW~AI
Foyers Primary substation 2018-19_completed |  | 0: 718~T1~AMPS~AI
Fraserburgh Primary substation 2018-19_completed |  | 0: 854~TR1~MW~AI; 1: 854~TR3~MW~AI; 2: 854A~C01~MW~AI
Friockheim Primary substation 2018-19_completed |  | 0: 089~T1_T2_11~AMPS~AI; 1: 089A~CO1~AMPS~AI; 2: 089B~C01~AMPS~AI
Fyvie Primary substation 2018-19 (11kV DG)_completed |  | 903B~C01~AMPS~AI | 856C~C01~AMPS~AI | 856A~C01~MW~AI | 856B~C01~AMPS~AI | 856~T1~MW~AI | 856~T2~MW~AI | 856~009~AMPS~AI | 856D~C01~AMPS~AI | 856E~C01~AMPS~AI
Gisla Primary substation 2018-19_completed |  | 648~1H0~AMPS~AI | 648~G1~KW~AI | 648~11KV_SYSTEM~KV~AI | 648~1H0~AMPS~AI | 648~G1~KVAR~AI | 648~G1~KW~AI
Glastullich Primary substation 2018-19_completed |  | 0: 522~11KV~AMPS~AI; 1: 522~11KV~KV~AI; 2: Cullise Gen not commissioned which affects peak & min demands.; 3: 522A~CO1~AMPS~AI
Glaxo 33kV Customer 2018-19 |  | 0: 071~3L5~AMPS~AI
Gledfield Primary Substation 2018-19_completed |  | 0: 523~T1~AMPS~AI; 1: 523~T1~AMPS~AI; 2: 523~T1~_~AI
Glencoe Primary substation 2018-19_completed |  | 330~001~AMPS~AI | 729~2L5~AMPS~AI | 330~001~AMPS~AI | 330~001~KV~AI | 330~001~MVAR~AI | 330~001~MW~AI
Glendevon Primary substation 2018-19_NEW FORMAT |  | 0: 251~4L5~AMPS~AI
Glendevon Primary substation 2018-19_NEW FORMAT_v2 |  | 0: 273~11KV~AMPS~AI
Glendoe Primary substation 2018-19_completed |  | 0: 781~002~AMPS~AI; 1: 781~003~AMPS~AI; 2: Add 2 above as removes needs to account for output from hydro Gen
Gleneagles Primary substation 2018-19_completed
Glensanda Primary substation 2018-19_completed |  | 0: 714~common~AMPS~AI; 1: 714~common~AMPS~AI
Golspie Primary substation 2018-19_completed |  | 0: 525~T1~MW~AI
Goodlyburn Primary substation 2018-19_completed |  | 0: 249~T1~MW~AI; 1: 249~T2~MW~AI
Gourdie Primary substation 2018-19_completed |  | 0: 004~TR1~AMPS~AI; 1: 004~TR1~MW~AI; 2: 004~TR1~AMPS~AI
Grantown Primary substation 2018-19_completed |  | 0: 722~T1_T2~AMPS~AI
Gremista Primary substation 2018-19_completed |  | 686~007~AMPS~AI | 686~021~AMPS~AI | 686~022~AMPS~AI | 686~023~AMPS~AI | 686~024~AMPS~AI | 686~025~AMPS~AI | 686~080~AMPS~AI | 686~088~AMPS~AI | 686~094~AMPS~AI | 686A~C01~AMPS~AI
Greyfriars Primary substation 2018-19_completed |  | 0: 861~TR1~AMPS~AI; 1: 861~TR2~AMPS~AI; 2: 861A~C01~AMPS~AI
Gutcher Primary substation 2018-19_completed |  | 0: 695~011~AMPS~AI
Halkirk Primary substation 2018-19 (MW Tags)_completed |  | 0: 597~TR1~MW~AI
Harvest Avenue Primary substation 2018-19 (MW Tags)_completed |  | 0: 991~TR1~MW~AI; 1: 991~TR2~MW~AI
Hastigrow Primary substation 2018-19_completed |  | 0: 582~TR1~AMPS~AI
Hatton Primary substation 2018-19 (MW Tags)_completed |  | 0: 863~T1~MW~AI; 1: 863~T2~MW~AI; 2: Replaced with; 3: 863~common~KV~AI; 4: Can also be used the PI Tags for the 11kV feeder (5)
Haudagain Primary substation 2018-19_completed |  | 0: 865~common~AMPS~AI; 1: 865~common~KV~AI
Hayton Primary substation 2018-19_completed |  | 867~T1~MW~AI | 867~T2~MW~AI | 867~005~AMPS~AI | 867~010~AMPS~AI | 867~011~AMPS~AI | 867~012~AMPS~AI | 867~BBAR~KV~AI | 867~T1~AMPS~AI
Helmsdale Primary substation 2018-19 (MW Tags)_completed |  | 0: 560~TR1~MW~AI
Hilton Primary substation 2018-19_completed |  | 0: 750~T1_T2~AMPS~AI
Hume Primary substation 2018-19_completed |  | 0: 067~T1_T2_11~AMPS~AI
Huntly Primary substation 2018-19 |  | 0: 869~common~AMPS~AI; 1: 869~common~KV~AI
Inchbare Primary substation 2018-19 |  | 0: 076~TR1~AMPS~AI
Innellan Primary substation 2018-19 |  | 379~SUMM~AMPS~AI | 379~BBAR~KV~AI | 379~002~AMPS~AI | 379~003~AMPS~AI | 379~005~AMPS~AI | 379~ACO~DC_FAIL~DI | 379~ACO~FAILED~DI | 379~BBAR~KV~AI
Insch Primary substation 2018-19 |  | 0: 871~common~AMPS~AI; 1: 871~NO1~KV~AI
Inveraray Primary substation 2018-19 (MW Tags) |  | 0: 321~TR1~MW~AI; 1: There have been works on this Primary during 17/18 and the load has been split between this Primary and Cromalt. For the 17/18, only the data after early feb 18 have been used to Provide Min and Max for this Primary
Inverarity Primary substation 2018-19 (MW Tags) |  | 0: 087~TR1~MW~AI; 1: 087~002~AMPS~AI; 2: 087~003~AMPS~AI; 3: 087~GT1_11~AMPS~AI
Inverarnie Primary substation 2018-19 |  | 0: 757~011~AMPS~AI; 1: There is no tag for Farr Hydro and this seems to mud the results
Inverbervie Primary substation 2018-19 (MW Tags) |  | 0: 873~TR1~MW~AI; 1: 873~TR2~MW~AI
Invergordon Primary substation 2018-19 (11kV DG) |  | 0: 559~T1_T2~AMPS~AI; 1: 559A~001~MW~AI; 2: 559A~002~MW~AI
Inverlochy Primary substation 2018-19 (11kV DG) |  | 724~TR1~MW~AI | 724~TR2~MW~AI | 724C~C01~AMPS~AI | 724C~C01~KV~AI | 724C~C01~MVAR~AI | MUCO~G1~MW~AI
Inverneil Primary substation 2018-19
Inverness Primary substation 2018-19 |  | 0: 725~T1_T2~AMPS~AI
Inverurie Primary substation 2018-19 |  | 0: 875~T1~MW~AI; 1: 875~T2~MW~AI; 2: 875~TR3~MW~AI; 3: 875A~C01~MW~AI; 4: 875B~C01~MW~AI
Kames Primary substation 2018-19 |  | 0: 366~11KV_SS~AMPS~AI; 1: 366~11KV_SS~AMPS~AI; 2: 366~11KV_SS~KV~AI
Keith Primary substation 2018-19 |  | 0: 463~T1~AMPS~AI; 1: 463~T2~AMPS~AI
Kemnay Primary substation 2018-19 |  | 0: 881~common~AMPS~AI
Kepculloch Primary substation 2018-19 |  | 0: 205~SUMM~AMPS~AI
Kerry Falls Primary substation 2018-19 (11kV DG) |  | 0: 531~080~AMPS~AI; 1: 531B~C01~AMPS~AI; 2: 531B~C01~KV~AI
Kilchrenan Primary substation 2018-19 |  | 0: 323~SS~AMPS~AI; 1: 323~common~KV~AI; 2: 323~SS~AMPS~AI; 3: B323R~common~AMPS~AI
Killearn Primary substation 2018-19 |  | 0: 204~T1~MW~AI
Killin Town Primary substation 2018-19 |  | 0: 219~011~AMPS~AI; 1: 219~011~AMPS~AI
Kilmelford Primary substation 2018-19 (11kV DG) |  | 0: 304~1T0~AMPS~AI; 1: KILM~G1~MW~AI; 2: 304~1T0~AMPS~AI; 3: 304~2L5~AMPS~AI
Kilninver Primary substation 2018-19 (11kV DG) |  | 0: 322~11KV_SS~AMPS~AI; 1: 322A~C01~AMPS~AI; 2: 322A~C01~KV~AI; 3: 322A~C01~MVAR~AI
Kiltarlity Primary substation 2018-19 |  | 0: 520~001~AMPS~AI; 1: 520~002~AMPS~AI
Kincorth Primary substation 2018-19 |  | 0: 934~7L5~MW~AI
Kingseat Primary substation 2018-19 |  | 0: 884~common~AMPS~AI; 1: 884~common~KV~AI; 2: 884B~C01~AMPS~AI; 3: 884B~C01~KV~AI
Kingussie Primary substation 2018-19 |  | 727~1H0~MW~AI | 727~2H0~MW~AI | 727~1H0~AMPS~AI | 727~1H0~KV~AI | 727~1H0~MVAR~AI | 727~1H0~MW~AI | 727~2H0~AMPS~AI | 727~2H0~KV~AI
Kinloch Primary substation 2018-19 |  | 333~T1~MW~AI | 333~PEAK~PERCENT~AI | 333~T1~AMPS~AI | 333~T1~KV~AI | 333~T1~MVAR~AI | 333~T1~MW~AI
Kinloch Rannoch Primary substation 2018-19 |  | 0: 262~011~AMPS~AI
Kinlochleven Primary substation 2018-19 |  | 0: 729~T1~MW~AI; 1: 729~T2~MW~AI
Kinloss Primary substation 2018-19 |  | 0: 453~T1_T2~AMPS~AI; 1: No tag
Kippen Primary substation 2018-19 |  | 0: 211~11KV~AMPS~AI; 1: 211~011~KV~AI
Kirkwall Primary substation 2018-19 |  | 677~T1~MW~AI | 677~T2~MW~AI | 677A~C01~MW~AI | 677A~C01~_~AI | 677A~C01~AMPS~AI | 677A~C01~KV~AI | 677A~C01~MVAR~AI
Kishorn Hill Primary substation 2018-19 |  | 0: 633~1H0~AMPS~AI; 1: 633~1H0~KV~AI
Kyle Primary substation 2018-19 |  | 0: 634~T1_T2~AMPS~AI
Lairg Primary substation 2018-19 (11kV DG) |  | 534~TR1~AMPS~AI | 534~11KV~KV~AI | 534A~1C0~AMPS~AI | 534A~1C0~KV~AI | 534A~1C0~MVAR~AI | 534A~1C0~MW~AI | 534A~WF~HZ~AI | 534A~WF~WIND_SPEED~AI
Latheron Primary substation 2018-19 |  | 0: 584~TR1~AMPS~AI
Laurencekirk Primary substation 2018-19 |  | 0: 890~TR1~MW~AI; 1: 890~TR2~MW~AI
Laxay Primary substation 2018-19 |  | 657~T1~AMPS~AI | 220~011~AMPS~AI | 265~common~AMPS~AI | 917~BBAR~KV~AI | 917~TR1~AMPS~AI | 917~TR2~AMPS~AI | 932~002~Amps~AI
Leoch Primary substation 2018-19 (11kV DG) |  | 090~TR1~MW~AI | 090B~C01~MW~AI | 090A~C01~MW~AI | 090D~C01~AMPS~AI | 090D~C01~KV~AI | 090C~C01~MW~AI
Lethen Primary Substation 2018-19 |  | 0: 703~T1~AMPS~AI
Lhanbryde Primary substation 2018-19 |  | 0: 488~T1_T2~AMPS~AI; 1: 488~T1_T2~KV~AI
Liddesdale Primary substation 2018-19 |  | 0: 721~016~AMPS~AI
Limehillocks Primary substation 2018-19 (11kV DG) |  | 0: 465~11KV~AMPS~AI; 1: 465A~C01~AMPS~AI; 2: 465A~C01~KV~AI; 3: 465A~C01~MW~AI
Lochaline Primary substation 2018-19 |  | 0: 747~T1_33KV~AMPS~AI; 1: 747~MULL_LOAD~MVA~AI; 2: 747~MULLLOAD~33AMPS~AI; 3: 747~T1_33KV~AMPS~AI
Lochdonhead Primary substation 2018-19
Lochearnhead Primary substation 2018-19 (11kV DG) |  | 217~common~AMPS~AI | 217A~C01~AMPS~AI | 217A~C01~KV~AI | 217A~C01~MW~AI | 217D~C01~AMPS~AI | 217D~C01~KV~AI
Lochee Primary substation 2018-19 |  | 0: 013~TR1~MW~AI; 1: 013~TR2~MW~AI
Lochgilphead Primary substation 2018-19
Lochgoilhead Primary substation 2018-19 |  | 0: 369~SS~AMPS~AI; 1: 369A~C01~AMPS~AI; 2: 369A~C01~KV~AI; 3: 369~T1~AMPS~AI
Lochinver Primary substation 2018-19 |  | 556~011~AMPS~AI | 556~011~AMPS~AI | 556~T1~_~AI | 556~T1~KV~AI | 556~T1~MW~AI | 556~T1~POWER~AI | 556~T1~VOLTS~AI
Lochside Primary substation 2018-19 |  | 0: 083~T1_T2_11~AMPS~AI
Logie Pert Primary substation 2018-19 |  | 0: 077~TR1~AMPS~AI; 1: 077~TR1~MW~AI
Longhaugh Primary substation 2018-19 |  | 054~T1_T2_T3~AMPS~AI | 054~BBAR~KV~AI | 054A~C01~AMPS~AI | 054A~C01~KV~AI | 054A~C01~MVAR~AI | 054A~C01~MW~AI
Lossiemouth Primary substation 2018-19 |  | 0: 455~T1_T2~AMPS~AI
Lower Ollach Primary substation 2018-19 |  | 0: 623~11KV~AMPS~AI
Lunanhead Primary substation 2018-19 (11kV DG) |  | 082~T1_T2_11~AMPS~AI | GEN473M_02 | 082A~C01~MW~AI | 082B~C01~MW~AI | 082C~C01~AMPS~AI | 082C~C01~KV~AI | 082D~C01~MW~AI
Lyndhurst Primary substation 2018-19 |  | 012~001~AMPS~AI | 012~002~AMPS~AI | 012~003~AMPS~AI | 012~004~AMPS~AI | 012~005~AMPS~AI | 012~006~AMPS~AI | 012~007~AMPS~AI | 012~008~AMPS~AI
Lyness Primary substation 2018-19 (11kV DG) |  | 0: 682~011~AMPS~AI
MacAlpine Road Primary substation 2018-19 |  | 014~TR1~MW~AI | 014~TR2~MW~AI | 014~001~AMPS~AI | 014~003~AMPS~AI | 014~005~AMPS~AI | 014~006~AMPS~AI
MacDuff Primary substation 2018-19 |  | 406~TR1~AMPS~AI | 406~TR2~AMPS~AI | 406A~C01~AMPS~AI | 406A~C01~KV~AI | 406A~C01~MVAR~AI | 406A~C01~MW~AI | 406B~C01~AMPS~AI | 406B~C01~KV~AI
Machrie Primary substation 2018-19 |  | 0: 373~011~AMPS~AI
Mallaig Primary substation 2018-19 |  | 0: 731~TR1~AMPS~AI
Markethill Primary substation 2018-19 (Disconnected) |  | 0: 742~011~AMPS~AI
Marnoch Primary substation 2018-19 |  | 0: 401~T1_T2~AMPS~AI
Marybank Primary substation 2018-19 |  | 0: 538~TR1~AMPS~AI; 1: 538~011~AMPS~AI; 2: 538~012~AMPS~AI; 3: 538~T1~_~AI; 4: 538~T1~AMPS~AI
Maryton Primary substation 2018-19 |  | 0: 084~T1_T2_11~AMPS~AI
Maud Primary substation 2018-19 |  | 901~common~AMPS~AI | 901~NO1~KV~AI | 901A~C01~AMPS~AI | 901A~C01~KV~AI | 901A~C01~MVAR~AI | 901A~C01~MW~AI
Melvich Primary substation 2018-19 |  | 0: 590~11KV~AMPS~AI
Menzieshill Primary Substation 2018-19 |  | 003~TR1~MW~AI | 003~TR2~MW~AI | 002~003~AMPS~AI | 003~001~AMPS~AI | 003~002~AMPS~AI | 003~003~AMPS~AI | 003~004~AMPS~AI | 003~005~AMPS~AI
Methlick Primary substation 2018-19 |  | 0: 903~TOTAL~AMPS~AI
Mid Yell Primary Substation 2018-19 |  | 0: 698~011~AMPS~AI
Midmar Primary substation 2018-19 |  | 0: 907~T1~AMPS~AI
Mill Road Primary substation 2018-19 |  | 0: 075~TR1~AMPS~AI
Milnathort Primary substation 2018-19 |  | 0: 251~011~AMPS~AI
Milton of Craigie Primary substation 2018-19 |  | 0: 052~TR1~MW~AI
Mintlaw Primary Substation 2018-19_run by VS |  | 0: 909~T1~MW~AI; 1: 909~T2~MW~AI; 2: 0; 3: 909B~CO1~MW~AI; 4: 909A~C01~MW~AI
Montrose North Primary substation 2018-19 |  | 0: 074~T1_T2_11~AMPS~AI
Mossat Primary substation 2018-19 |  | 0: 911~common~AMPS~AI
Mount Pleasant Primary substation 2018-19 |  | 0: 585~T1~AMPS~AI
Muir of Ord substation 2018-19 |  | 0: 547~T1_T2~AMPS~AI
Muirend Primary substation 2018-19 |  | 0: 542~TR1~AMPS~AI
Nairn Central Primary substation 2018-19 |  | 0: 733~1L5~AMPS~AI
New Pitsligo Primary substation 2018-19 (11kV DG) |  | 0: 913~common~AMPS~AI
Newtonhill Primary 2018-19 |  | 0: 915~common~AMPS~AI
Nigg Primary 2018-19 |  | 0: 554~TR1~AMPS~AI
Ninewells Primary 2018-19 |  | 0: 006~004~AMPS~AI
North Kessock Primary 2018-19 |  | 0: 558~TR1~AMPS~AI
North Muirton Primary 2018-19 |  | 0: 272~SS_11~AMPS~AI
North Street Primary 2018-19 |  | 0: 929~common~AMPS~AI
Northfield Primary 2018-19 |  | 0: 917~TR1~AMPS~AI
Nostie Bridge Primary 2018-19 |  | 0: 636~T1~AMPS~AI
Oban Primary 2018-19 |  | 0: 307~TR1~AMPS~AI
Old Craigie Road Primary 2018-19 |  | 0: 053~T2~AMPS~AI
Oldmeldrum primary 2018-19 |  | 0: 921~common~AMPS~AI
Ormlie Primary 2018-19 |  | 0: 587~T1~AMPS~AI
Otter Ferry Primary 2018-19 |  | 0: 375~11KV_SS~AMPS~AI
Overgate Primary 2018-19 |  | 0: 024~TR1~AMPS~AI
Park Primary 2018-19 |  | 0: 923~TR1~AMPS~AI
Peddieston Primary 2018-19 |  | 0: 553~T1~AMPS~AI
Perth Harbour Primary 2018-19 |  | 0: 247~T1~AMPS~AI
Peterhead Grange Primary 2018-19 |  | 0: 928~001~AMPS~AI
Peterhead Shell Primary 2018-19 |  | 0: PEHS~GT~MW~AI
Pinegrove Primary 2018-19 |  | 0: 734~T1_T2~AMPS~AI
Pitlochry Primary 2018-19 |  | 0: 263~TR1~AMPS~AI
Pollachar Primary 2018-19 |  | 0: 660~TR1~AMPS~AI
Port Askaig Primary 2018-19 |  | 0: 334~common~AMPS~AI
Port Ellen Primary 2018-19 |  | 0: 331~common~AMPS~AI
Portree Primary 2018-19 |  | 0: 632~T1~AMPS~AI
Portsoy Primary 2018-19 |  | 0: 435~TR2~AMPS~AI
Queens Lane North Primary 2018-19 |  | 0: 932~TR1~Amps~AI
Quoich Primary substation 2018-19 |  | 0: 748~1L5~MW~AI
Raigmore Primary 2018-19 |  | 0: 735~014~AMPS~AI
Redford Primary 2018-19 |  | 0: 066~T1_11~AMPS~AI
Redgordon Primary 2018-19 |  | 0: 270~common~AMPS~AI
Redmoss Primary 2018-19 |  | 0: 935~TR1~AMPS~AI
Rhiconich Primary 2018-19 |  | 0: 544~T1_T2~AMPS~AI
Rosebank Primary 2018-19 |  | 0: 033~TR1~AMPS~AI
Rothes Primary 2018-19 |  | 0: 459~T1_T2~AMPS~AI
Rothesay Primary 2018-19 |  | 0: 362~T1_T2~AMPS~AI
Rousay Primary 2018-19 |  | 0: 498~011~MW~AI
Ruthrieston Primary substation 2018-19 |  | 0: CRAI~QLN2~AMPS~AI
Salen 2 Primary 2018-19 |  | 0: 749~T1~AMPS~AI
Salen, Mull Primary 2018-19 |  | 0: 315~TR1~AMPS~AI
Sanday Primary 2018-19 |  | 0: 685~011~AMPS~AI
Sandbank Primary substation 2018-19 |  | 0: 364~002~AMPS~AI; 1: 364~003~AMPS~AI; 2: 364~004~AMPS~AI; 3: 364~005~AMPS~AI
Scalloway Primary substation 2018-19 |  | 0: 697~011~AMPS~AI; 1: 693~T1~AMPS~AI; 2: 696~1L5_33~AMPS~AI
Scone Primary substation 2018-19 |  | 0: 271~common~AMPS~AI; 1: 271~common~KV~AI; 2: GEN418_2
Scottish Power Interconnector (3L5) 2018-19 |  | 0: 241~3L5~AMPS~AI
Setter Sandwick Primary substation 2018-19 |  | 0: 693~T1~AMPS~AI; 1: 693~T1~KV~AI
Shapinsay Primary substation 2018-19 |  | 0: 683~011~AMPS~AI; 1: 683~11~AMPS~AI
Shetland Gas Plant 33kV Customer 2018-19 |  | 0: 696~1C0~AMPS~AI
Shieldaig Primary substation 2018-19 (11kV DG) |  | 0: 641~11KV~AMPS~AI
Shin Primary substation 2018-19 |  | 0: 545~T3~MW~AI; 1: 545A~1C0~MW~AI; 2: 545B~1C0~MW~AI
Skene Primary substation 2018-19 |  | 0: 941~TR1~MW~AI; 1: 941~TR2~MW~AI; 2: 941~TR1~MW~AI; 3: 941~TR2~MW~AI
Skulamus Primary substation 2018-19 |  | 0: 639~T1~AMPS~AI; 1: 639~T1~KV~AI
Springhill Primary substation 2018-19 |  | 0: WOHI~1L5~AMPS~AI; 1: YWOHI~2L5~AMPS~AI; 2: WOHI~5L5~AMPS~AI; 3: WOHI~7L5~AMPS~AI
St Cyrus Primary substation 2018-19 (11kV DG) |  | 952~common~AMPS~AI | 952~common~KV~AI | 952A~C01~MW~AI | 952D~C01~MW~AI | 952E~C01~AMPS~AI | 952E~C01~KV~AI | 952F~C01~AMPS~AI | 952F~C01~KV~AI
St Fergus Gas Primary substation 2018-19 (11kV DG) |  | 0: SFEG~GT1~MW~AI; 1: SFEG~GT2~MW~AI; 2: 955A~C01~MW~AI; 3: 955B~C01~MW~AI; 4: 955C~C01~MW~AI
St Fillans 33kV Load 2018-19 |  | 0: LEDP~G1~MW~AI
St Machar Primary substation 2018-19 (11kV DG) |  | 0: 956~TR1~AMPS~AI; 1: 956~TR2~AMPS~AI; 2: 956~TR1~KV~AI
St Mary's Primary substation 2018-19 (11kV DG) |  | 679~TR1~AMPS~AI | 679B~C01~KV~AI | 679B~C01~MVAR~AI | 679B~C01~MW~AI | 679B~C01~VOLTS~AI | 679B~DSTAT_SPC~KV~AI | 679B~DSTAT_SPC~VOLTS~AI
St Nicholas Primary substation 2018-19 |  | 0: 958~TR1~AMPSB~AI
Stockinish Primary substation 2018-19 |  | 0: 658~MW~MW~AI
Stonehaven Primary substation 2018-19 (11kV DG) |  | 945~T1~AMPS~AI | 945~T2~AMPS~AI | 945B~C01~AMPS~AI | 945B~C01~KV~AI | 945C~C01~AMPS~AI | 945C~C01~KV~AI | 890A~C01~MW~AI
Stoneywood T1 & T2 Primary substation 2018-19 |  | 0: 947~TR1~AMPS~AI; 1: 947~TR1~KV~AI; 2: 947~TR2~AMPS~AI; 3: 947~TR2~KV~AI
Stoneywood T3 Primary substation 2018-19 |  | 0: 947~TR3~MW~AI
Strachur Primary substation 2018-19 |  | 0: 382~11KV~AMPS~AI
Strathdon Primary substation 2018-19 |  | 0: 951~TR1~AMPS~AI
Strichen Primary substation 2018-19 (11kV DG) |  | 949~T1~MW~AI | 949~T2~MW~AI | 950A~C01~AMPS~AI | 950A~C01~KV~AI | 950B~C01~MW~AI | 950C~C01~MW~AI | 950D~C01~MW~AI | 950E~C01~MW~AI | 950F~C01~MW~AI
Stromness Primary substation 2018-19 (11kV DG) |  | 0: 678~TR1~MW~AI; 1: 678~TR2~MW~AI; 2: 678A~C01~MW~AI; 3: 678~096~MW~AI
Stronsay Primary substation 2018-19 |  | 0: 684~011~AMPS~AI
Strontian Primary substation 2018-19 |  | 0: 751~11KV~AMPS~AI
Sumburgh Primary substation 2018-19 |  | 0: 697~011~AMPS~AI
Tain Primary substation 2018-19 |  | 0: 546~T1_T2~AMPS~AI
Tarbert (Harris) Primary substation 2018-19 |  | 0: 658~MW~MW~AI; 1: 662~T1_T2~AMPS~AI
Tarbert Loch Fyne Primary substation 2018-19 |  | 310~TR1~MW~AI | 310~TR2~MW~AI | 310A~C01~AMPS~AI | 310A~C01~AMPS~AI | 310A~C01~KV~AI | 310~TR1~MW~AI | 310~TR2~MW~AI | 310A~C01~AMPS~AI | 310A~C01~AMPS~AI | 310A~C01~KV~AI
Taynuilt Primary substation 2018-19
Thimblerow Primary substation 2018-19 |  | 248~002~AMPS~AI | 248~003~AMPS~AI | 248~005~AMPS~AI | 248~006~AMPS~AI | 248~007~AMPS~AI | 248~008~AMPS~AI | 248~009~AMPS~AI | 248~010~AMPS~AI | 248~011~AMPS~AI | 248~012~AMPS~AI
Tomatin Primary substation 2018-19 |  | 0: 738~1H0~AMPS~AI; 1: 738~1H0~KV~AI
Torryburn Primary substation 2018-19 |  | 962~T1~AMPS~AI | 962~T2~AMPS~AI | 962~T2~KV~AI | 962A~C01~AMPS~AI | 962A~C01~KV~AI | 962B~C01~AMPS~AI | 962B~C01~KV~AI | 306~T1~AMPS~AI
Tumblin Primary substation 2018-19 |  | \\pipsnorth\790~T2~KV~AI | 790~011~AMPS~AI | 790~012~AMPS~AI | 790~013~AMPS~AI | 790~common~AMPS~AI | 790~T2~AMPS~AI | 790~T2~KV~AI
Tummel Bridge Primary substation 2018-19 |  | 0: 260~T2_11~AMPS~AI; 1: 260~T2_11~KV~AI
Turriff Primary substation 2018-19 (11kV DG) |  | 964E~C01~MW~AI | 964F~C01~MW~AI | 964G~C01~MW~AI | 964H~C01~AMPS~AI | 964H~C01~KV~AI | 964J~C01~MW~AI | 964K~C01~AMPS~AI | 964K~C01~KV~AI
Tyndrum Primary substation 2018-19 (11kV DG) |  | 0: Auchertyre; 1: Inverhaggernie Burn Hydro
Uig Primary substation 2018-19 |  | 0: 640~11KV~AMPS~AI; 1: 640~011~AMPS~AI; 2: 640~012~AMPS~AI; 3: 640~T1~KV~AI
Ullapool Primary substation 2018-19 |  | 0: 549~071~AMPS~AI; 1: 549~072~AMPS~AI
Unst Primary substation 2018-19 |  | 0: 791~common~AMPS~AI
Voe Primary substation 2018-19 |  | 687~common~AMPS~AI | 687~common~KV~AI | 687~046~AMPS~AI | 687~047~AMPS~AI | 687~052~AMPS~AI | 687~053~AMPS~AI
Walton Primary substation 2018-19 |  | 0: 025~T2_T3_11~AMPS~AI; 1: 025~011~KV~AI
Waterloo Primary substation 2018-19 |  | 0: 741~T1_T2~AMPS~AI
West Kirkton Primary substation 2018-19 |  | 0: 015~T2_T3~AMPS~AI
West Parkfergus Primary substation 2018-19 |  | 0: 349~11KV_LOAD~AMPS~AI; 1: 349~11KV~KV~AI
Westray Primary substation 2018-19 (11kV DG) |  | 0: 674~001~AMPS~AI
Whitehouse Primary substation 2018-19 |  | 0: TARL~3L5~MW~AI
Whitestripes Primary substation 2018-19
Whiting Bay Primary substation 2018-19 |  | 0: 371~T1_11KV~AMPS~AI; 1: 371~common~KV~AI
Wick Primary substation 2018-19 |  | 0: 594~TR1~MW~AI; 1: 594~TR2~MW~AI
Woodhill Primary Substation 2018-2019 |  | 986~TR3~AMPS~AI | 986~TR1~KV~AI | 986~TR3~KV~AI | 986B~C01~MW~AI | 986C~C02~MW~AI | 986~T1~AMPS~AI | 986~T3~AMPS~AI

## Sheet2
Chaorach Primary substation 2018-19 | 140~001~AMPS~AI
Coupar Angus Primary substation 2018-19 | 243~1H0~AMPS~AI | 243~2H0~AMPS~AI | 243~1H0~MW~AI | 243~2H0~MW~AI
Dounreay Primary substation 2018-19 | 598~T1~MW~AI | 598~T2~MW~AI | 598~1S0~AMPS~AI | 598~1S0~KV~AI | 598~1S0~MVAR~AI | 598~1S0~MW~AI | 598~6L5~AMPS~AI | 598~6L5~KV~AI
Dunvegan Primary substation 2018-19_completed | 638~T1~AMPS~AI
Firth Primary substation 2018-19_completed | 692~T2_11KV~AMPS~AI | 692~11KV~KV~AI
Glaxo 33kV Customer 2018-19 | 071~3L5~AMPS~AI
Glendevon Primary substation 2018-19_NEW FORMAT | 251~4L5~AMPS~AI
Gremista Primary substation 2018-19_completed | 686~007~AMPS~AI | 686~021~AMPS~AI | 686~022~AMPS~AI | 686~023~AMPS~AI | 686~024~AMPS~AI | 686~025~AMPS~AI | 686~080~AMPS~AI | 686~088~AMPS~AI
Greyfriars Primary substation 2018-19_completed | 861~TR1~AMPS~AI | 861~TR2~AMPS~AI | 861A~C01~AMPS~AI
Gutcher Primary substation 2018-19_completed | 695~011~AMPS~AI
Harvest Avenue Primary substation 2018-19 (MW Tags)_completed | 991~TR1~MW~AI | 991~TR2~MW~AI
Inverness Primary substation 2018-19 | 725~T1_T2~AMPS~AI
Keith Primary substation 2018-19 | 463~T1~AMPS~AI | 463~T2~AMPS~AI
Kinlochleven Primary substation 2018-19 | 729~T1~MW~AI | 729~T2~MW~AI
Lairg Primary substation 2018-19 (11kV DG) | 534~TR1~AMPS~AI | 534~11KV~KV~AI | 534A~1C0~AMPS~AI | 534A~1C0~KV~AI | 534A~1C0~MVAR~AI | 534A~1C0~MW~AI | 534A~WF~HZ~AI
Mid Yell Primary Substation 2018-19 | 698~011~AMPS~AI
Perth Harbour Primary 2018-19 | 247~T1~AMPS~AI
Peterhead Shell Primary 2018-19 | PEHS~GT~MW~AI
Scalloway Primary substation 2018-19 | 697~011~AMPS~AI | 693~T1~AMPS~AI | 696~1L5_33~AMPS~AI
Scottish Power Interconnector (3L5) 2018-19 | 241~3L5~AMPS~AI
Setter Sandwick Primary substation 2018-19 | 693~T1~AMPS~AI | 693~T1~KV~AI
Shetland Gas Plant 33kV Customer 2018-19 | 696~1C0~AMPS~AI
St Fergus Gas Primary substation 2018-19 (11kV DG) | SFEG~GT1~MW~AI | SFEG~GT2~MW~AI | 955A~C01~MW~AI | 955B~C01~MW~AI | 955C~C01~MW~AI
St Fillans 33kV Load 2018-19 | LEDP~G1~MW~AI
Sumburgh Primary substation 2018-19 | 697~011~AMPS~AI
Tumblin Primary substation 2018-19 | \\pipsnorth\790~T2~KV~AI | 790~011~AMPS~AI | 790~012~AMPS~AI | 790~013~AMPS~AI | 790~common~AMPS~AI | 790~T2~AMPS~AI | 790~T2~KV~AI
Tummel Bridge Primary substation 2018-19 | 260~T2_11~AMPS~AI | 260~T2_11~KV~AI
Unst Primary substation 2018-19 | 791~common~AMPS~AI
Voe Primary substation 2018-19 | 687~common~AMPS~AI | 687~common~KV~AI | 687~046~AMPS~AI | 687~047~AMPS~AI | 687~052~AMPS~AI | 687~053~AMPS~AI
265~common~AMPS~AI | 917~BBAR~KV~AI | 917~TR1~AMPS~AI | 917~TR2~AMPS~AI | 932~002~Amps~AI
Glaxo 33kV Customer 2018-19 | 071~3L5~AMPS~AI
Broadford Primary substation 2018-19 (MW Tags) | 627~T1~MW~AI
Coupar Angus Primary substation 2018-19 | 243~1H0~AMPS~AI | 243~2H0~AMPS~AI | 243~1H0~MW~AI | 243~2H0~MW~AI
BP Balbeggie 33kV Customer 2018-19 | 243~5L5~AMPS~AI
Craigton Primary substation 2018-19 | CRAI~CBL1~AMPS~AI
| Dunvegan Primary substation 2018-19_completed | 638~T1~AMPS~AI
| Harvest Avenue Primary substation 2018-19 (MW Tags)_completed | 991~TR1~MW~AI | 991~TR2~MW~AI
Fasnakyle Primary substation 2018-19_completed | FASN~T5~AMPS~AI
Chaorach Primary substation 2018-19 | 140~001~AMPS~AI
Lairg Primary substation 2018-19 (11kV DG) | 534~TR1~AMPS~AI | 534~11KV~KV~AI | 534A~1C0~AMPS~AI | 534A~1C0~KV~AI | 534A~1C0~MVAR~AI | 534A~1C0~MW~AI | 534A~WF~HZ~AI | 534A~WF~WIND_SPEED~AI
003~005~AMPS~AI
Cromalt Primary substation 2018-19 (MW Tags) | 326~TR1~MW~AI
Craiginches Primary substation 2018-19 | 832~TR1~MW~AI | 832~TR2~MW~AI
Settlements Data | 267A~C01~AMPS~AI
Tummel Bridge Primary substation 2018-19 | 260~T2_11~AMPS~AI | 260~T2_11~KV~AI